## Instructions
EAV64332 | V1.5 | ATV600 - Communication Parameters
WARNING
UNEXPECTED MOVEMENT Drive systems may perform unexpected movements because of incorrect wiring, incorrect settings, incorrect data or other errors. • Only appropriately trained persons who are familiar with and understand the contents of all pertinent product documentation and who have received safety training to recognize and avoid hazards involved are authorized to work on and with this drive system. Installation, adjustment, repair and maintenance must be performed by qualified personnel. • Carefully install the wiring in accordance with the EMC requirements. • Do not operate the product with unknown or unsuitable settings or data. • Perform a comprehensive commissioning test. Failure to follow these instructions can result in death, serious injury, or equipment damage.
WARNING
LOSS OF CONTROL • The designer of any control scheme must consider the potential failure modes of control paths and, for critical control functions, provide a means to achieve a safe state during and after a path failure. Examples of critical control functions are emergency stop, overtravel stop, power outage and restart. • Separate or redundant control paths must be provided for critical control functions. • System control paths may include communication links. Consideration must be given to the implications of unanticipated transmission delays or failures of the link. • Observe all accident prevention regulations and local safety guidelines (1). • Each implementation of the product must be individually and thoroughly tested for proper operation before being placed into service. Failure to follow these instructions can result in death, serious injury, or equipment damage.
(1) For USA: Additional information, refer to NEMA ICS 1.1 (latest edition), Safety Guidelines for the Application, Installation, and Maintenance of Solid State Control and to NEMA ICS 7.1 (latest edition), Safety Standards for Construction and Guide for Selection, Installation and Operation of Adjustable-Speed Drive Systems.
Electrical equipment should be installed, operated, serviced, and maintained only by qualified personnel. No responsibility is assumed by Schneider Electric for any consequences arising out of the use of this material.
EXPLANATORY NOTE
This Excel file is for reference only. Refer to programming manual and communication protocols manuals for full information.
This Excel file can be used to carry out searches (example: parameter address and format) and sort operations.
The columns include the following criteria:
Code: Language-independent, this allows a rapid search in the programming manual.
Additional information can be found in the Fieldbus Manuals (Modbus, CANopen....etc.....)
Name: Parameter designation
Logic address: Address for the Modbus messaging are in decimal and hexadecimal (preceded by 16#) format.
To optimize Modbus messaging performance, two addresses are given for the control word (CMD) and the status word (ETA).
The addresses annotated "speed" are for use in rpm; the addresses annotated "frequency" are for use in Hz.
CANopen index: CANopen index/subindex in hexadecimal format, to be used for variable assignment of PDOs and SDO messaging.
PROFIBUS index: Address for PROFIBUS
CIP : Address for DeviceNet
Class/instance/attribute in decimal and hexadecimal (preceded by 16#) format.
When two paths are given, for example:
- 16#29/01/0D = 41/1/13 (messaging): ODVA standard path. It can be used for explicit messaging. Do not use it for configuring an assembly.
- 16#8C/01/07 = 140/1/7 (assembly): Altivar-specific path. This is the path that must be used for configuring an assembly. Avoid using it for explicit messaging, to ensure better interchangeability.
Link: For WORD type parameters, a dynamic link opens the description of a bit register or a listing. Listings are common to several parameters; only one part is valid for a given parameter. Refer to programming manual to determine the valid values. If an invalid value is written to a configuration parameter, the drive will indicate a fault [Invalid config.] (CFI).
Category: Defines the role of the parameter, for example: Command parameter, Status parameter, etc.
Access: Read and write options:
R: Read only
R/W: Read and write
R/WS: Read and write (write only possible when the drive is not in RUN mode).
It is not possible to write these parameters in "5-Operation enabled" or "6-Quick stop active" states.
If the parameter is written in the "4-Switched on" state, transition 10 to "2-Switch on disabled" is activated.
Type:
WORD (bit register): Word where each bit represents a command or a state
WORD (listing): Word where each value represents a possible choice for a configuration or state
INT: Signed integer
UINT: Unsigned integer
DINT: Signed double integer
UDINT: Unsigned double integer
Units: Physical unit and multiplier
Factory setting: Value of the parameter set at the factory.
Range: Possible values
Display: Parameter name displayed on the graphic display terminal, in square brackets [---], and parameter code displayed by the 7-segment digits on the integrated display terminal, in round brackets (---).
Menu: Indicates the menus or menus where the parameter is located. Menu name displayed on the graphic display terminal, in square brackets [---], and menu code displayed by the 7-segment digits on the integrated display terminal (if existing), in round brackets (---).
Order: Gives the initial storage order of the parameter in the file, from 1 to n. This makes it possible, after sorting operations, to put this file back in its initial order by sorting the column in ascending order.

## Parameters
Code | Name | Logic address | CANopen index | DeviceNet path | Link | Category | Access | Type | Units | Factory setting | Range | Display | Menu | Order
CMI | Extended control word | 16#2138 = 8504 | 16#2037/5 | 16#8B/01/69 = 139/01/105 | - | Control parameters | R/W | WORD (BitString16) | - |  | - |  |  | 1
CMD | Cmd Register | 16#2135 = 8501 | 16#2037/2 | 16#8B/01/66 = 139/01/102 | CMD | Control parameters | R/W | WORD (BitString16) | - |  | - | [Cmd Register] (CMd) | [Communication map] (CMM-) | 2
RPR | Time Counter Reset | 16#0C30 = 3120 | 16#2001/15 | 16#70/01/79 = 112/01/121 | RPR | Control parameters | R/W | WORD (Enumeration) | - | [No] (nO) | - | [Time Counter Reset] (rPr) | [Counter Management] (ELt-) [Maintenance] (CSMA-) | 3
LFRD | Speed setpoint | 16#219A = 8602 | 16#2038/3 | 16#8C/01/03 = 140/01/03 | - | Setpoint parameters | R/W | INT (Signed16) | 1 rpm | 0 rpm | -32767 ... 32767 |  |  | 4
LFR | Ref Frequency | 16#2136 = 8502 | 16#2037/3 | 16#8B/01/67 = 139/01/103 | - | Setpoint parameters | R/W | INT (Signed16) | 0.1 Hz | 0.0 Hz | -500.0 Hz ... 500.0 Hz | [Ref Frequency] (LFr) | [Drive parameters] (MPI-) [Display] (SUP-) | 5
PISP | PID Set Point | 16#2137 = 8503 | 16#2037/4 | 16#8B/01/68 = 139/01/104 | - | Setpoint parameters | R/W | UINT (Unsigned16) | 1 |  | 0 ... 1000 |  |  | 6
AIV1 | AIV1 Image input | 16#14A1 = 5281 | 16#2016/52 | 16#7B/01/52 = 123/01/82 | - | Setpoint parameters | R/W | INT (Signed16) | 1 | 0 | -8192 ... 8192 | [AIV1 Image input] (AIU1) | [Drive parameters] (MPI-) | 7
MFR | Multiplying coeff. | 16#2E37 = 11831 | 16#2058/20 | 16#9C/01/20 = 156/01/32 | - | Setpoint parameters | R/W | UINT (Unsigned16) | 1 % |  | 0 % ... 100 % | [Multiplying coeff.] (MFr) | [Drive parameters] (MPI-) [Settings] (SEt-) | 8
ETA | CIA402 State Reg | 16#0C81 = 3201 | 16#2002/2 | 16#71/01/02 = 113/01/02 | ETA | Status parameters | R | WORD (BitString16) | - |  | - | [CIA402 State Reg] (EtA) | [Communication map] (CMM-) | 9
HMIS | Drive State | 16#0CA8 = 3240 | 16#2002/29 | 16#71/01/29 = 113/01/41 | HMIS | Status parameters | R | WORD (Enumeration) | - |  | - |  |  | 10
ETI | Internal State Reg | 16#0C86 = 3206 | 16#2002/7 | 16#71/01/07 = 113/01/07 | ETI | Status parameters | R | WORD (BitString16) | - |  | - |  |  | 11
CRC | Ref Freq Channel | 16#20F9 = 8441 | 16#2036/2A | 16#8B/01/2A = 139/01/42 | CRC | Status parameters | R | WORD (BitString16) | - |  | - |  |  | 12
CCC | Active command channel | 16#20FA = 8442 | 16#2036/2B | 16#8B/01/2B = 139/01/43 | CCC | Status parameters | R | WORD (BitString16) | - |  | - |  |  | 13
CNFS | Config. active | 16#1F54 = 8020 | 16#2032/15 | 16#89/01/15 = 137/01/21 | CNFS | Status parameters | R | WORD (Enumeration) | - |  | - | [Config. active] (CnFS) | [Drive parameters] (MPI-) [Display] (SUP-) | 14
STUN | Tune selection | 16#2591 = 9617 | 16#2042/12 | 16#91/01/12 = 145/01/18 | STUN | Status parameters | [always] | WORD (Enumeration) | - | [Default] (tAb) | - | [Tune selection] (StUn) | [Simply start] (SIM-) [Motor tune] (MtU-) | 15
SMOT | Saliency mot. state | 16#25AD = 9645 | 16#2042/2E | 16#91/01/2E = 145/01/46 | SMOT | Status parameters | R | WORD (Enumeration) | - |  | - | [Saliency mot. state] (SMOt) | [Motor tune] (MtU-) | 16
RFRD | Output velocity | 16#219C = 8604 | 16#2038/5 | 16#8C/01/05 = 140/01/05 | - | Actual values parameters | R | INT (Signed16) | 1 rpm |  | -32767 ... 32767 |  |  | 17
RFR | Motor Frequency | 16#0C82 = 3202 | 16#2002/3 | 16#71/01/03 = 113/01/03 | - | Actual values parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Motor Frequency] (rFr) | [Drive parameters] (MPI-) [Display] (SUP-) | 18
OTR | Motor torque | 16#0C85 = 3205 | 16#2002/6 | 16#71/01/06 = 113/01/06 | - | Actual values parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Motor torque] (Otr) | [Motor parameters] (MMO-) [Display] (SUP-) | 19
LCR | Motor Current | 16#0C84 = 3204 | 16#2002/5 | 16#71/01/05 = 113/01/05 | - | Actual values parameters | R | UINT (Unsigned16) | Refer to programming manual |  | Depends of rating | [Motor Current] (LCr) | [Pump Dashboard] (PMt-) [Fan Dashboard] (FAn-) [Motor parameters] (MMO-) [Display] (SUP-) | 20
UOP | Motor voltage | 16#0C88 = 3208 | 16#2002/9 | 16#71/01/09 = 113/01/09 | - | Actual values parameters | R | UINT (Unsigned16) | 1 V |  | 0 V ... 65535 V | [Motor voltage] (UOP) | [Motor parameters] (MMO-) [Display] (SUP-) | 21
OPR | Motor Power | 16#0C8B = 3211 | 16#2002/C | 16#71/01/0C = 113/01/12 | - | Actual values parameters | R | INT (Signed16) | 1 % |  | -32767 % ... 32767 % | [Motor Power] (OPr) | [Motor parameters] (MMO-) [Display] (SUP-) | 22
FRHD | Speed reference before ramp | 16#219D = 8605 | 16#2038/6 | 16#8C/01/06 = 140/01/06 | - | Reference parameters | R | INT (Signed16) | 1 rpm |  | -32767 ... 32767 |  |  | 23
FROD | Speed reference after ramp | 16#21C1 = 8641 | 16#2038/2A | 16#8C/01/2A = 140/01/42 | - | Reference parameters | R | INT (Signed16) | 1 rpm |  | -32767 ... 32767 |  |  | 24
FRH | Pre-Ramp Ref Freq | 16#0C83 = 3203 | 16#2002/4 | 16#71/01/04 = 113/01/04 | - | Reference parameters | R | INT (Signed16) | 0.1 Hz |  | -500.0 Hz ... 500.0 Hz | [Pre-Ramp Ref Freq] (FrH) | [Pump Dashboard] (PMt-) [Fan Dashboard] (FAn-) [Drive parameters] (MPI-) [Communication map] (CMM-) [Display] (SUP-) | 25
FRO | Frequency reference after ramp | 16#233D = 9021 | 16#203C/16 | 16#8E/01/16 = 142/01/22 | - | Reference parameters | R | INT (Signed16) | 0.1 Hz |  | -32767 ... 32767 |  |  | 26
RPC | PID reference | 16#2ECE = 11982 | 16#2059/53 | 16#9C/01/B7 = 156/01/183 | - | Reference parameters | R | UINT (Unsigned16) | Refer to programming manual |  | Refer to programming manual | [PID reference] (rPC) | [Control] (Ctr-) [Control] (Ftr-) [PID display] (PIC-) [Application Parameters] (APr-) [Display] (SUP-) | 27
RPF | PID feedback | 16#2ECD = 11981 | 16#2059/52 | 16#9C/01/B6 = 156/01/182 | - | Reference parameters | R | UINT (Unsigned16) | Refer to programming manual |  | Refer to programming manual | [PID feedback] (rPF) | [Control] (Ctr-) [Control] (Ftr-) [PID display] (PIC-) [Feedback] (Fdb-) [Display] (SUP-) | 28
RPE | PID Error | 16#2ECC = 11980 | 16#2059/51 | 16#9C/01/B5 = 156/01/181 | - | Reference parameters | R | INT (Signed16) | Refer to programming manual |  | Refer to programming manual | [PID Error] (rPE) | [PID display] (PIC-) [Display] (SUP-) | 29
RPO | PID Output | 16#2ECF = 11983 | 16#2059/54 | 16#9C/01/B8 = 156/01/184 | - | Reference parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [PID Output] (rPO) | [PID display] (PIC-) [Display] (SUP-) | 30
ULN | Mains Voltage | 16#0C87 = 3207 | 16#2002/8 | 16#71/01/08 = 113/01/08 | - | Measurement parameters | R | UINT (Unsigned16) | 0.1 V |  | [No meas.] (----) ... 6553.5 V | [Mains Voltage] (ULn) | [Drive parameters] (MPI-) [Display] (SUP-) | 31
THD | Drive Therm State | 16#0C89 = 3209 | 16#2002/A | 16#71/01/0A = 113/01/10 | - | Measurement parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 200 % | [Drive Therm State] (tHd) | [Drive parameters] (MPI-) [Display] (SUP-) | 32
THR | Motor Therm State | 16#259E = 9630 | 16#2042/1F | 16#91/01/1F = 145/01/31 | - | Measurement parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 200 % | [Motor Therm State] (tHr) | [Pump Dashboard] (PMt-) [Fan Dashboard] (FAn-) [Motor parameters] (MMO-) [Display] (SUP-) | 33
RTH | Motor Run Time | 16#0CAC = 3244 | 16#2002/2D | 16#71/01/2D = 113/01/45 |  | Measurement parameters | R/WS | UINT (Unsigned32) | - |  | - | [Motor Run Time] (rtH) | [Counter Management] (ELt-) [Variable Speed Pump] (MPP-) [Display] (SUP-) | 34
PTH | Power-on time | 16#0CAE = 3246 | 16#2002/2F | 16#71/01/2F = 113/01/47 |  | Measurement parameters | R/WS | UINT (Unsigned32) | - |  | - | [Power-on time] (PtH) | [Counter Management] (ELt-) | 35
IL1R | Logic inputs states | 16#1452 = 5202 | 16#2016/3 | 16#7B/01/03 = 123/01/03 | IL1R | I/O parameters | R | WORD (BitString16) | - |  | - |  |  | 36
OL1R | Logic outputs states | 16#145C = 5212 | 16#2016/D | 16#7B/01/0D = 123/01/13 | OL1R | I/O parameters | R/W | WORD (BitString16) | - |  | - |  |  | 37
AI1C | AI1 | 16#147A = 5242 | 16#2016/2B | 16#7B/01/2B = 123/01/43 | - | I/O parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [AI1] (AI1C) | [Display] (SUP-) | 38
AI1R | Analog input 1 standardized value | 16#1470 = 5232 | 16#2016/21 | 16#7B/01/21 = 123/01/33 | - | I/O parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767 |  |  | 39
AI2C | AI2 | 16#147B = 5243 | 16#2016/2C | 16#7B/01/2C = 123/01/44 | - | I/O parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [AI2] (AI2C) | [Display] (SUP-) | 40
AI2R | Analog input 2 standardized value | 16#1471 = 5233 | 16#2016/22 | 16#7B/01/22 = 123/01/34 | - | I/O parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767 |  |  | 41
AI3C | AI3 | 16#147C = 5244 | 16#2016/2D | 16#7B/01/2D = 123/01/45 | - | I/O parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [AI3] (AI3C) | [Display] (SUP-) | 42
AI3R | Analog input 3 standardized value | 16#1472 = 5234 | 16#2016/23 | 16#7B/01/23 = 123/01/35 | - | I/O parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767 |  |  | 43
AO1C | AQ1 | 16#1497 = 5271 | 16#2016/48 | 16#7B/01/48 = 123/01/72 | - | I/O parameters | R/W | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [AQ1] (AO1C) | [Display] (SUP-) | 44
AO1R | Analog output 1 standardized value | 16#148D = 5261 | 16#2016/3E | 16#7B/01/3E = 123/01/62 | - | I/O parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767 |  |  | 45
ERRD | CiA402 fault code | 16#219E = 8606 | 16#2038/7 | 16#8C/01/07 = 140/01/07 | ERRD | Fault parameters | R | WORD (BitString16) | - |  | - |  |  | 46
LFT | Last Error | 16#1BD1 = 7121 | 16#2029/16 | 16#84/01/7A = 132/01/122 | LFT | Fault parameters | R | WORD (Enumeration) | - |  | - | [Last Error] (LFt) | [Diag. data] (ddt-) | 47
CIC | Incorrect configuration | 16#1BDA = 7130 | 16#2029/1F | 16#84/01/83 = 132/01/131 | CIC | Fault parameters | R/WS | WORD (BitString16) | - |  | - |  |  | 48
CNF | Fieldbus Com Interrupt | 16#1BDC = 7132 | 16#2029/21 | 16#84/01/85 = 132/01/133 | - | Fault parameters | [always] | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Fieldbus Com Interrupt] (CnF) | [DEVICENET DIAG] (dUn-) [PROFIBUS DIAG] (Prb-) [PROFINET DIAG] (Prn-) | 49
ILF1 | InternCom Error1 | 16#1BDE = 7134 | 16#2029/23 | 16#84/01/87 = 132/01/135 | - | Fault parameters | [always] | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [InternCom Error1] (ILF1) | [PROFIBUS DIAG] (Prb-) [PROFINET DIAG] (Prn-) | 50
FNB | Fault counter | 16#1CE1 = 7393 | 16#202B/5E | 16#85/01/C2 = 133/01/194 | - | Fault parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 51
DP0 | Fault code on last fault | 16#1C20 = 7200 | 16#202A/1 | 16#85/01/01 = 133/01/01 | LFT | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 52
ULP0 | DC bus voltage | 16#1C66 = 7270 | 16#202A/47 | 16#85/01/47 = 133/01/71 | - | History parameters | R | UINT (Unsigned16) | 0.1 V |  | [No meas.] (----) ... 6553.5 V |  |  | 53
LCP0 | Motor current | 16#1C48 = 7240 | 16#202A/29 | 16#85/01/29 = 133/01/41 | - | History parameters | R | INT (Signed16) | Refer to programming manual |  | Depends of rating |  |  | 54
RFP0 | Output frequency | 16#1C52 = 7250 | 16#202A/33 | 16#85/01/33 = 133/01/51 | - | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz |  |  | 55
THP0 | Motor therm state | 16#1C70 = 7280 | 16#202A/51 | 16#85/01/51 = 133/01/81 | - | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % |  |  | 56
EP0 | ETA state word | 16#1C2A = 7210 | 16#202A/B | 16#85/01/0B = 133/01/11 | EP0 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 57
IP0 | ETI state word | 16#1C34 = 7220 | 16#202A/15 | 16#85/01/15 = 133/01/21 | IP0 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 58
CMP0 | Cmd word | 16#1C3E = 7230 | 16#202A/1F | 16#85/01/1F = 133/01/31 | CMP0 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 59
DCC0 | Command Channel | 16#FB2C = 64300 |  | = | CNL | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 60
DRC0 | Ref Freq Channel | 16#FB36 = 64310 |  | = | CNL | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 61
CRP0 | Channels active on last fault | 16#1C7A = 7290 | 16#202A/5B | 16#85/01/5B = 133/01/91 | CRP0 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 62
RTP0 | Elapsed time | 16#1C5C = 7260 | 16#202A/3D | 16#85/01/3D = 133/01/61 | - | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h |  |  | 63
OTP0 | Motor Torque | 16#1CA2 = 7330 | 16#202B/1F | 16#85/01/83 = 133/01/131 | - | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % |  |  | 64
TDP0 | Drive Thermal State | 16#1CAC = 7340 | 16#202B/29 | 16#85/01/8D = 133/01/141 | - | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 % |  |  | 65
TJP0 | IGBT Junction Temp | 16#1CB6 = 7350 | 16#202B/33 | 16#85/01/97 = 133/01/151 | - | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C |  |  | 66
SFP0 | Switching Frequency | 16#1CC0 = 7360 | 16#202B/3D | 16#85/01/A1 = 133/01/161 | - | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz |  |  | 67
DP1 | Fault code on fault n-1 | 16#1C21 = 7201 | 16#202A/2 | 16#85/01/02 = 133/01/02 | LFT | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 68
ULP1 | DC bus voltage | 16#1C67 = 7271 | 16#202A/48 | 16#85/01/48 = 133/01/72 | - | History parameters | R | UINT (Unsigned16) | 0.1 V |  | [No meas.] (----) ... 6553.5 V |  |  | 69
LCP1 | Motor current | 16#1C49 = 7241 | 16#202A/2A | 16#85/01/2A = 133/01/42 | - | History parameters | R | INT (Signed16) | Refer to programming manual |  | Depends of rating |  |  | 70
RFP1 | Output frequency | 16#1C53 = 7251 | 16#202A/34 | 16#85/01/34 = 133/01/52 | - | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz |  |  | 71
THP1 | Motor therm state | 16#1C71 = 7281 | 16#202A/52 | 16#85/01/52 = 133/01/82 | - | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % |  |  | 72
EP1 | Last Error 1 Status | 16#1C2B = 7211 | 16#202A/C | 16#85/01/0C = 133/01/12 | EP1 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 73
IP1 | ETI state word | 16#1C35 = 7221 | 16#202A/16 | 16#85/01/16 = 133/01/22 | IP1 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 74
CMP1 | Cmd word | 16#1C3F = 7231 | 16#202A/20 | 16#85/01/20 = 133/01/32 | CMP1 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 75
DCC1 | Command Channel | 16#FB2D = 64301 |  | = | CNL | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 76
DRC1 | Ref Freq Channel | 16#FB37 = 64311 |  | = | CNL | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 77
CRP1 | Active channels on fault n-1 | 16#1C7B = 7291 | 16#202A/5C | 16#85/01/5C = 133/01/92 | CRP1 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 78
RTP1 | Elapsed time | 16#1C5D = 7261 | 16#202A/3E | 16#85/01/3E = 133/01/62 | - | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h |  |  | 79
OTP1 | Motor Torque | 16#1CA3 = 7331 | 16#202B/20 | 16#85/01/84 = 133/01/132 | - | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % |  |  | 80
TDP1 | Drive Thermal State | 16#1CAD = 7341 | 16#202B/2A | 16#85/01/8E = 133/01/142 | - | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 % |  |  | 81
TJP1 | IGBT Junction Temp | 16#1CB7 = 7351 | 16#202B/34 | 16#85/01/98 = 133/01/152 | - | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C |  |  | 82
SFP1 | Switching Frequency | 16#1CC1 = 7361 | 16#202B/3E | 16#85/01/A2 = 133/01/162 | - | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz |  |  | 83
DP2 | Fault code on fault n-2 | 16#1C22 = 7202 | 16#202A/3 | 16#85/01/03 = 133/01/03 | LFT | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 84
ULP2 | DC bus voltage | 16#1C68 = 7272 | 16#202A/49 | 16#85/01/49 = 133/01/73 | - | History parameters | R | UINT (Unsigned16) | 0.1 V |  | [No meas.] (----) ... 6553.5 V |  |  | 85
LCP2 | Motor current | 16#1C4A = 7242 | 16#202A/2B | 16#85/01/2B = 133/01/43 | - | History parameters | R | INT (Signed16) | Refer to programming manual |  | Depends of rating |  |  | 86
RFP2 | Output frequency | 16#1C54 = 7252 | 16#202A/35 | 16#85/01/35 = 133/01/53 | - | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz |  |  | 87
THP2 | Motor therm state | 16#1C72 = 7282 | 16#202A/53 | 16#85/01/53 = 133/01/83 | - | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % |  |  | 88
EP2 | Last Error 2 Status | 16#1C2C = 7212 | 16#202A/D | 16#85/01/0D = 133/01/13 | EP2 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 89
IP2 | ETI state word | 16#1C36 = 7222 | 16#202A/17 | 16#85/01/17 = 133/01/23 | IP2 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 90
CMP2 | Cmd word | 16#1C40 = 7232 | 16#202A/21 | 16#85/01/21 = 133/01/33 | CMP2 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 91
DCC2 | Command Channel | 16#FB2E = 64302 |  | = | CNL | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 92
DRC2 | Ref Freq Channel | 16#FB38 = 64312 |  | = | CNL | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 93
CRP2 | Active channels on fault n-2 | 16#1C7C = 7292 | 16#202A/5D | 16#85/01/5D = 133/01/93 | CRP2 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 94
RTP2 | Elapsed time | 16#1C5E = 7262 | 16#202A/3F | 16#85/01/3F = 133/01/63 | - | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h |  |  | 95
OTP2 | Motor Torque | 16#1CA4 = 7332 | 16#202B/21 | 16#85/01/85 = 133/01/133 | - | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % |  |  | 96
TDP2 | Drive Thermal State | 16#1CAE = 7342 | 16#202B/2B | 16#85/01/8F = 133/01/143 | - | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 % |  |  | 97
TJP2 | IGBT Junction Temp | 16#1CB8 = 7352 | 16#202B/35 | 16#85/01/99 = 133/01/153 | - | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C |  |  | 98
SFP2 | Switching Frequency | 16#1CC2 = 7362 | 16#202B/3F | 16#85/01/A3 = 133/01/163 | - | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz |  |  | 99
DP3 | Fault code on fault n-3 | 16#1C23 = 7203 | 16#202A/4 | 16#85/01/04 = 133/01/04 | LFT | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 100
ULP3 | DC bus voltage | 16#1C69 = 7273 | 16#202A/4A | 16#85/01/4A = 133/01/74 | - | History parameters | R | UINT (Unsigned16) | 0.1 V |  | [No meas.] (----) ... 6553.5 V |  |  | 101
LCP3 | Motor current | 16#1C4B = 7243 | 16#202A/2C | 16#85/01/2C = 133/01/44 | - | History parameters | R | INT (Signed16) | Refer to programming manual |  | Depends of rating |  |  | 102
RFP3 | Output frequency | 16#1C55 = 7253 | 16#202A/36 | 16#85/01/36 = 133/01/54 | - | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz |  |  | 103
THP3 | Motor therm state | 16#1C73 = 7283 | 16#202A/54 | 16#85/01/54 = 133/01/84 | - | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % |  |  | 104
EP3 | Last Error 3 Status | 16#1C2D = 7213 | 16#202A/E | 16#85/01/0E = 133/01/14 | EP3 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 105
IP3 | ETI state word | 16#1C37 = 7223 | 16#202A/18 | 16#85/01/18 = 133/01/24 | IP3 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 106
CMP3 | Cmd word | 16#1C41 = 7233 | 16#202A/22 | 16#85/01/22 = 133/01/34 | CMP3 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 107
DCC3 | Command Channel | 16#FB2F = 64303 |  | = | CNL | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 108
DRC3 | Ref Freq Channel | 16#FB39 = 64313 |  | = | CNL | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 109
CRP3 | Active channels on fault n-3 | 16#1C7D = 7293 | 16#202A/5E | 16#85/01/5E = 133/01/94 | CRP3 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 110
RTP3 | Elapsed time | 16#1C5F = 7263 | 16#202A/40 | 16#85/01/40 = 133/01/64 | - | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h |  |  | 111
OTP3 | Motor Torque | 16#1CA5 = 7333 | 16#202B/22 | 16#85/01/86 = 133/01/134 | - | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % |  |  | 112
TDP3 | Drive Thermal State | 16#1CAF = 7343 | 16#202B/2C | 16#85/01/90 = 133/01/144 | - | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 % |  |  | 113
TJP3 | IGBT Junction Temp | 16#1CB9 = 7353 | 16#202B/36 | 16#85/01/9A = 133/01/154 | - | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C |  |  | 114
SFP3 | Switching Frequency | 16#1CC3 = 7363 | 16#202B/40 | 16#85/01/A4 = 133/01/164 | - | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz |  |  | 115
DP4 | Fault code on fault n-4 | 16#1C24 = 7204 | 16#202A/5 | 16#85/01/05 = 133/01/05 | LFT | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 116
ULP4 | DC bus voltage | 16#1C6A = 7274 | 16#202A/4B | 16#85/01/4B = 133/01/75 | - | History parameters | R | UINT (Unsigned16) | 0.1 V |  | [No meas.] (----) ... 6553.5 V |  |  | 117
LCP4 | Motor current | 16#1C4C = 7244 | 16#202A/2D | 16#85/01/2D = 133/01/45 | - | History parameters | R | INT (Signed16) | Refer to programming manual |  | Depends of rating |  |  | 118
RFP4 | Output frequency | 16#1C56 = 7254 | 16#202A/37 | 16#85/01/37 = 133/01/55 | - | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz |  |  | 119
THP4 | Motor therm state | 16#1C74 = 7284 | 16#202A/55 | 16#85/01/55 = 133/01/85 | - | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % |  |  | 120
EP4 | Last Error 4 Status | 16#1C2E = 7214 | 16#202A/F | 16#85/01/0F = 133/01/15 | EP4 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 121
IP4 | ETI state word | 16#1C38 = 7224 | 16#202A/19 | 16#85/01/19 = 133/01/25 | IP4 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 122
CMP4 | Cmd word | 16#1C42 = 7234 | 16#202A/23 | 16#85/01/23 = 133/01/35 | CMP4 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 123
DCC4 | Command Channel | 16#FB30 = 64304 |  | = | CNL | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 124
DRC4 | Ref Freq Channel | 16#FB3A = 64314 |  | = | CNL | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 125
CRP4 | Active channels on fault n-4 | 16#1C7E = 7294 | 16#202A/5F | 16#85/01/5F = 133/01/95 | CRP4 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 126
RTP4 | Elapsed time | 16#1C60 = 7264 | 16#202A/41 | 16#85/01/41 = 133/01/65 | - | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h |  |  | 127
OTP4 | Motor Torque | 16#1CA6 = 7334 | 16#202B/23 | 16#85/01/87 = 133/01/135 | - | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % |  |  | 128
TDP4 | Drive Thermal State | 16#1CB0 = 7344 | 16#202B/2D | 16#85/01/91 = 133/01/145 | - | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 % |  |  | 129
TJP4 | IGBT Junction Temp | 16#1CBA = 7354 | 16#202B/37 | 16#85/01/9B = 133/01/155 | - | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C |  |  | 130
SFP4 | Switching Frequency | 16#1CC4 = 7364 | 16#202B/41 | 16#85/01/A5 = 133/01/165 | - | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz |  |  | 131
DP5 | Fault code on fault n-5 | 16#1C25 = 7205 | 16#202A/6 | 16#85/01/06 = 133/01/06 | LFT | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 132
ULP5 | DC bus voltage | 16#1C6B = 7275 | 16#202A/4C | 16#85/01/4C = 133/01/76 | - | History parameters | R | UINT (Unsigned16) | 0.1 V |  | [No meas.] (----) ... 6553.5 V |  |  | 133
LCP5 | Motor current | 16#1C4D = 7245 | 16#202A/2E | 16#85/01/2E = 133/01/46 | - | History parameters | R | INT (Signed16) | Refer to programming manual |  | Depends of rating |  |  | 134
RFP5 | Output frequency | 16#1C57 = 7255 | 16#202A/38 | 16#85/01/38 = 133/01/56 | - | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz |  |  | 135
THP5 | Motor therm state | 16#1C75 = 7285 | 16#202A/56 | 16#85/01/56 = 133/01/86 | - | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % |  |  | 136
EP5 | ETA state word | 16#1C2F = 7215 | 16#202A/10 | 16#85/01/10 = 133/01/16 | EP5 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 137
IP5 | ETI state word | 16#1C39 = 7225 | 16#202A/1A | 16#85/01/1A = 133/01/26 | IP5 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 138
CMP5 | Cmd word | 16#1C43 = 7235 | 16#202A/24 | 16#85/01/24 = 133/01/36 | CMP5 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 139
DCC5 | Command Channel | 16#FB31 = 64305 |  | = | CNL | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 140
DRC5 | Ref Freq Channel | 16#FB3B = 64315 |  | = | CNL | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 141
CRP5 | Active channels on fault n-5 | 16#1C7F = 7295 | 16#202A/60 | 16#85/01/60 = 133/01/96 | CRP5 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 142
RTP5 | Elapsed time | 16#1C61 = 7265 | 16#202A/42 | 16#85/01/42 = 133/01/66 | - | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h |  |  | 143
OTP5 | Motor Torque | 16#1CA7 = 7335 | 16#202B/24 | 16#85/01/88 = 133/01/136 | - | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % |  |  | 144
TDP5 | Drive Thermal State | 16#1CB1 = 7345 | 16#202B/2E | 16#85/01/92 = 133/01/146 | - | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 % |  |  | 145
TJP5 | IGBT Junction Temp | 16#1CBB = 7355 | 16#202B/38 | 16#85/01/9C = 133/01/156 | - | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C |  |  | 146
SFP5 | Switching Frequency | 16#1CC5 = 7365 | 16#202B/42 | 16#85/01/A6 = 133/01/166 | - | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz |  |  | 147
DP6 | Fault code on fault n-6 | 16#1C26 = 7206 | 16#202A/7 | 16#85/01/07 = 133/01/07 | LFT | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 148
ULP6 | DC bus voltage | 16#1C6C = 7276 | 16#202A/4D | 16#85/01/4D = 133/01/77 | - | History parameters | R | UINT (Unsigned16) | 0.1 V |  | [No meas.] (----) ... 6553.5 V |  |  | 149
LCP6 | Motor current | 16#1C4E = 7246 | 16#202A/2F | 16#85/01/2F = 133/01/47 | - | History parameters | R | INT (Signed16) | Refer to programming manual |  | Depends of rating |  |  | 150
RFP6 | Output frequency | 16#1C58 = 7256 | 16#202A/39 | 16#85/01/39 = 133/01/57 | - | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz |  |  | 151
THP6 | Motor therm state | 16#1C76 = 7286 | 16#202A/57 | 16#85/01/57 = 133/01/87 | - | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % |  |  | 152
EP6 | ETA state word | 16#1C30 = 7216 | 16#202A/11 | 16#85/01/11 = 133/01/17 | EP6 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 153
IP6 | ETI state word | 16#1C3A = 7226 | 16#202A/1B | 16#85/01/1B = 133/01/27 | IP6 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 154
CMP6 | Cmd word | 16#1C44 = 7236 | 16#202A/25 | 16#85/01/25 = 133/01/37 | CMP6 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 155
DCC6 | Command Channel | 16#FB32 = 64306 |  | = | CNL | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 156
DRC6 | Ref Freq Channel | 16#FB3C = 64316 |  | = | CNL | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 157
CRP6 | Active channels on fault n-6 | 16#1C80 = 7296 | 16#202A/61 | 16#85/01/61 = 133/01/97 | CRP6 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 158
RTP6 | Elapsed time | 16#1C62 = 7266 | 16#202A/43 | 16#85/01/43 = 133/01/67 | - | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h |  |  | 159
OTP6 | Motor Torque | 16#1CA8 = 7336 | 16#202B/25 | 16#85/01/89 = 133/01/137 | - | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % |  |  | 160
TDP6 | Drive Thermal State | 16#1CB2 = 7346 | 16#202B/2F | 16#85/01/93 = 133/01/147 | - | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 % |  |  | 161
TJP6 | IGBT Junction Temp | 16#1CBC = 7356 | 16#202B/39 | 16#85/01/9D = 133/01/157 | - | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C |  |  | 162
SFP6 | Switching Frequency | 16#1CC6 = 7366 | 16#202B/43 | 16#85/01/A7 = 133/01/167 | - | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz |  |  | 163
DP7 | Fault code on fault n-7 | 16#1C27 = 7207 | 16#202A/8 | 16#85/01/08 = 133/01/08 | LFT | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 164
ULP7 | DC bus voltage | 16#1C6D = 7277 | 16#202A/4E | 16#85/01/4E = 133/01/78 | - | History parameters | R | UINT (Unsigned16) | 0.1 V |  | [No meas.] (----) ... 6553.5 V |  |  | 165
LCP7 | Motor current | 16#1C4F = 7247 | 16#202A/30 | 16#85/01/30 = 133/01/48 | - | History parameters | R | INT (Signed16) | Refer to programming manual |  | Depends of rating |  |  | 166
RFP7 | Output frequency | 16#1C59 = 7257 | 16#202A/3A | 16#85/01/3A = 133/01/58 | - | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz |  |  | 167
THP7 | Motor therm state | 16#1C77 = 7287 | 16#202A/58 | 16#85/01/58 = 133/01/88 | - | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % |  |  | 168
EP7 | ETA state word | 16#1C31 = 7217 | 16#202A/12 | 16#85/01/12 = 133/01/18 | EP7 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 169
IP7 | ETI state word | 16#1C3B = 7227 | 16#202A/1C | 16#85/01/1C = 133/01/28 | IP7 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 170
CMP7 | Cmd word | 16#1C45 = 7237 | 16#202A/26 | 16#85/01/26 = 133/01/38 | CMP7 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 171
DCC7 | Command Channel | 16#FB33 = 64307 |  | = | CNL | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 172
DRC7 | Ref Freq Channel | 16#FB3D = 64317 |  | = | CNL | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 173
CRP7 | Active channels on fault n-7 | 16#1C81 = 7297 | 16#202A/62 | 16#85/01/62 = 133/01/98 | CRP7 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 174
RTP7 | Elapsed time | 16#1C63 = 7267 | 16#202A/44 | 16#85/01/44 = 133/01/68 | - | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h |  |  | 175
OTP7 | Motor Torque | 16#1CA9 = 7337 | 16#202B/26 | 16#85/01/8A = 133/01/138 | - | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % |  |  | 176
TDP7 | Drive Thermal State | 16#1CB3 = 7347 | 16#202B/30 | 16#85/01/94 = 133/01/148 | - | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 % |  |  | 177
TJP7 | IGBT Junction Temp | 16#1CBD = 7357 | 16#202B/3A | 16#85/01/9E = 133/01/158 | - | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C |  |  | 178
SFP7 | Switching Frequency | 16#1CC7 = 7367 | 16#202B/44 | 16#85/01/A8 = 133/01/168 | - | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz |  |  | 179
DP8 | Fault code on fault n-8 | 16#1C28 = 7208 | 16#202A/9 | 16#85/01/09 = 133/01/09 | LFT | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 180
ULP8 | DC bus voltage | 16#1C6E = 7278 | 16#202A/4F | 16#85/01/4F = 133/01/79 | - | History parameters | R | UINT (Unsigned16) | 0.1 V |  | [No meas.] (----) ... 6553.5 V |  |  | 181
LCP8 | Motor current | 16#1C50 = 7248 | 16#202A/31 | 16#85/01/31 = 133/01/49 | - | History parameters | R | INT (Signed16) | Refer to programming manual |  | Depends of rating |  |  | 182
RFP8 | Output frequency | 16#1C5A = 7258 | 16#202A/3B | 16#85/01/3B = 133/01/59 | - | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz |  |  | 183
THP8 | Motor therm state | 16#1C78 = 7288 | 16#202A/59 | 16#85/01/59 = 133/01/89 | - | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % |  |  | 184
EP8 | ETA state word | 16#1C32 = 7218 | 16#202A/13 | 16#85/01/13 = 133/01/19 | EP8 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 185
IP8 | ETI state word | 16#1C3C = 7228 | 16#202A/1D | 16#85/01/1D = 133/01/29 | IP8 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 186
CMP8 | Cmd word | 16#1C46 = 7238 | 16#202A/27 | 16#85/01/27 = 133/01/39 | CMP8 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 187
DCC8 | Command Channel | 16#FB34 = 64308 |  | = | CNL | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 188
DRC8 | Ref Freq Channel | 16#FB3E = 64318 |  | = | CNL | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 189
CRP8 | Active channels on fault n-8 | 16#1C82 = 7298 | 16#202A/63 | 16#85/01/63 = 133/01/99 | CRP8 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 190
RTP8 | Elapsed time | 16#1C64 = 7268 | 16#202A/45 | 16#85/01/45 = 133/01/69 | - | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h |  |  | 191
OTP8 | Motor Torque | 16#1CAA = 7338 | 16#202B/27 | 16#85/01/8B = 133/01/139 | - | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % |  |  | 192
TDP8 | Drive Thermal State | 16#1CB4 = 7348 | 16#202B/31 | 16#85/01/95 = 133/01/149 | - | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 % |  |  | 193
TJP8 | IGBT Junction Temp | 16#1CBE = 7358 | 16#202B/3B | 16#85/01/9F = 133/01/159 | - | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C |  |  | 194
SFP8 | Switching Frequency | 16#1CC8 = 7368 | 16#202B/45 | 16#85/01/A9 = 133/01/169 | - | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz |  |  | 195
NCV | DrvNomRating | 16#0BC3 = 3011 | 16#2000/C | 16#70/01/0C = 112/01/12 | NCV | Identification parameters | R | WORD (Enumeration) | - | [Unknown rating] (nO) | - |  |  | 196
VCAL | Drive mains Voltage | 16#0BC4 = 3012 | 16#2000/D | 16#70/01/0D = 112/01/13 | VCAL | Identification parameters | R | WORD (Enumeration) | - | [Unknown Voltage] (nO) | - |  |  | 197
INV | Nom Drive Current | 16#0BC9 = 3017 | 16#2000/12 | 16#70/01/12 = 112/01/18 | - | Identification parameters | [always] | UINT (Unsigned16) | Refer to programming manual | Depends of rating | 0 ... 65535 |  |  | 198
VDP | Drv.Soft.Ver | 16#0CE6 = 3302 | 16#2003/3 | 16#71/01/67 = 113/01/103 | - | Identification parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 199
PAN0 | Device name (char 1 and 2) | 16#0D0C = 3340 | 16#2003/29 | 16#71/01/8D = 113/01/141 | - | Identification parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 200
PAN1 | Device name (char 3 and 4) | 16#0D0D = 3341 | 16#2003/2A | 16#71/01/8E = 113/01/142 | - | Identification parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 201
PAN2 | Device name (char 5 and 6) | 16#0D0E = 3342 | 16#2003/2B | 16#71/01/8F = 113/01/143 | - | Identification parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 202
PAN3 | Device name (char 7 and 8) | 16#0D0F = 3343 | 16#2003/2C | 16#71/01/90 = 113/01/144 | - | Identification parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 203
PAN4 | Device name (char 9 and 10) | 16#0D10 = 3344 | 16#2003/2D | 16#71/01/91 = 113/01/145 | - | Identification parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 204
PAN5 | Device name (char 11 and 12) | 16#0D11 = 3345 | 16#2003/2E | 16#71/01/92 = 113/01/146 | - | Identification parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 205
PAN6 | Device name (char 13 and 14) | 16#0D12 = 3346 | 16#2003/2F | 16#71/01/93 = 113/01/147 | - | Identification parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 206
PAN7 | Device name (char 15 and 16) | 16#0D13 = 3347 | 16#2003/30 | 16#71/01/94 = 113/01/148 | - | Identification parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 207
NC1 | Com Scan Out1 val. | 16#31D9 = 12761 | 16#2061/3E | 16#A0/01/A2 = 160/01/162 | - | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out1 val.] (nC1) | [Com scan output map] (OSA-) | 208
NC2 | Com Scan Out2 val. | 16#31DA = 12762 | 16#2061/3F | 16#A0/01/A3 = 160/01/163 | - | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out2 val.] (nC2) | [Com scan output map] (OSA-) | 209
NC3 | Com Scan Out3 val. | 16#31DB = 12763 | 16#2061/40 | 16#A0/01/A4 = 160/01/164 | - | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out3 val.] (nC3) | [Com scan output map] (OSA-) | 210
NC4 | Com Scan Out4 val. | 16#31DC = 12764 | 16#2061/41 | 16#A0/01/A5 = 160/01/165 | - | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out4 val.] (nC4) | [Com scan output map] (OSA-) | 211
NC5 | Com Scan Out5 val. | 16#31DD = 12765 | 16#2061/42 | 16#A0/01/A6 = 160/01/166 | - | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out5 val.] (nC5) | [Com scan output map] (OSA-) | 212
NC6 | Com Scan Out6 val. | 16#31DE = 12766 | 16#2061/43 | 16#A0/01/A7 = 160/01/167 | - | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out6 val.] (nC6) | [Com scan output map] (OSA-) | 213
NC7 | Com Scan Out7 val. | 16#31DF = 12767 | 16#2061/44 | 16#A0/01/A8 = 160/01/168 | - | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out7 val.] (nC7) | [Com scan output map] (OSA-) | 214
NC8 | Com Scan Out8 val. | 16#31E0 = 12768 | 16#2061/45 | 16#A0/01/A9 = 160/01/169 | - | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out8 val.] (nC8) | [Com scan output map] (OSA-) | 215
NM1 | Com Scan In1 val. | 16#31C5 = 12741 | 16#2061/2A | 16#A0/01/8E = 160/01/142 | - | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In1 val.] (nM1) | [Com. scanner input map] (ISA-) | 216
NM2 | Com Scan In2 val. | 16#31C6 = 12742 | 16#2061/2B | 16#A0/01/8F = 160/01/143 | - | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In2 val.] (nM2) | [Com. scanner input map] (ISA-) | 217
NM3 | Com Scan In3 val. | 16#31C7 = 12743 | 16#2061/2C | 16#A0/01/90 = 160/01/144 | - | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In3 val.] (nM3) | [Com. scanner input map] (ISA-) | 218
NM4 | Com Scan In4 val. | 16#31C8 = 12744 | 16#2061/2D | 16#A0/01/91 = 160/01/145 | - | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In4 val.] (nM4) | [Com. scanner input map] (ISA-) | 219
NM5 | Com Scan In5 val. | 16#31C9 = 12745 | 16#2061/2E | 16#A0/01/92 = 160/01/146 | - | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In5 val.] (nM5) | [Com. scanner input map] (ISA-) | 220
NM6 | Com Scan In6 val. | 16#31CA = 12746 | 16#2061/2F | 16#A0/01/93 = 160/01/147 | - | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In6 val.] (nM6) | [Com. scanner input map] (ISA-) | 221
NM7 | Com Scan In7 val. | 16#31CB = 12747 | 16#2061/30 | 16#A0/01/94 = 160/01/148 | - | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In7 val.] (nM7) | [Com. scanner input map] (ISA-) | 222
NM8 | Com Scan In8 val. | 16#31CC = 12748 | 16#2061/31 | 16#A0/01/95 = 160/01/149 | - | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In8 val.] (nM8) | [Com. scanner input map] (ISA-) | 223
SMAL | Velocity min amount | 16#21A1 = 8609 | 16#2038/A | 16#8C/01/0A = 140/01/10 |  | CiA 402 settings | R/W | UINT (Unsigned32) | - |  | - |  |  | 224
SMIL | Velocity max amount | 16#219F = 8607 | 16#2038/8 | 16#8C/01/08 = 140/01/08 |  | CiA 402 settings | R/W | UINT (Unsigned32) | - |  | - |  |  | 225
SPAL | Acceleration delta speed | 16#21A3 = 8611 | 16#2038/C | 16#8C/01/0C = 140/01/12 |  | CiA 402 settings | R/W | UINT (Unsigned32) | - |  | - |  |  | 226
SPAT | Acceleration delta time | 16#21A5 = 8613 | 16#2038/E | 16#8C/01/0E = 140/01/14 | - | CiA 402 settings | R/W | UINT (Unsigned16) | 1 s |  | 0 s ... 65535 s |  |  | 227
SPDL | Deceleration delta speed | 16#21A6 = 8614 | 16#2038/F | 16#8C/01/0F = 140/01/15 |  | CiA 402 settings | R/W | UINT (Unsigned32) | - |  | - |  |  | 228
SPFN | Setpoint factor numerator | 16#21C2 = 8642 | 16#2038/2B | 16#8C/01/2B = 140/01/43 | - | CiA 402 settings | R/WS | INT (Signed16) | 1 | 1 | -32768 ... 32767 |  |  | 229
SPFD | Setpoint factor denominator | 16#21C3 = 8643 | 16#2038/2C | 16#8C/01/2C = 140/01/44 | - | CiA 402 settings | R/WS | INT (Signed16) | 1 | 1 | -32768 ... 32767 |  |  | 230
DOTD | SwitchOnDisable Stp | 16#21CC = 8652 | 16#2038/35 | 16#8C/01/35 = 140/01/53 | DOTD | CiA 402 settings | R/WS | WORD (Enumeration) | - | [Ramp stop] (rMP) | - | [SwitchOnDisable Stp] (dOtd) | [Stop configuration] (Stt-) | 231
QSTD | Quick stop option code | 16#21CB = 8651 | 16#2038/34 | 16#8C/01/34 = 140/01/52 | QSTD | CiA 402 settings | R/WS | WORD (Enumeration) | - | (FSt2) | - |  |  | 232
SCS | Save configuration | 16#1F41 = 8001 | 16#2032/2 | 16#89/01/02 = 137/01/02 | SCS | Configuration management | R/WS | WORD (Enumeration) | - | [No] (nO) | - | (SCS) | [Factory settings] (FCS-) | 233
FCS | Restore configuration | 16#1F42 = 8002 | 16#2032/3 | 16#89/01/03 = 137/01/03 | FCS | Configuration management | [gatingOff] | WORD (Enumeration) | - | (nO) | - | (FCS) | [Factory settings] (FCS-) | 234
FRY | Factory setting group | 16#0BCE = 3022 | 16#2000/17 | 16#70/01/17 = 112/01/23 | FRY | Configuration management | [gatingOff] | WORD (BitString16) | - | 0 | - |  |  | 235
CHA1 | 2 Parameter sets | 16#3266 = 12902 | 16#2063/3 | 16#A1/01/67 = 161/01/103 | PSLIN | Parameter set switching | R/WS | WORD (Enumeration) | - | [Not Assigned] (nO) | - | [2 Parameter sets] (CHA1) | [Parameters switching] (MLP-) | 236
CHA2 | 3 Parameter sets | 16#3267 = 12903 | 16#2063/4 | 16#A1/01/68 = 161/01/104 | PSLIN | Parameter set switching | R/WS | WORD (Enumeration) | - | [Not Assigned] (nO) | - | [3 Parameter sets] (CHA2) | [Parameters switching] (MLP-) | 237
CFPS | Used param. set | 16#3264 = 12900 | 16#2063/1 | 16#A1/01/65 = 161/01/101 | CFPS | Parameter set switching | R | WORD (Enumeration) | - |  | - | [Used param. set] (CFPS) | [Drive parameters] (MPI-) [Display] (SUP-) | 238
VAL | Load parameter set command | 16#3265 = 12901 | 16#2063/2 | 16#A1/01/66 = 161/01/102 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 1 |  |  | 239
AD01 | Parameter set address 1 | 16#326F = 12911 | 16#2063/C | 16#A1/01/70 = 161/01/112 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 240
AD02 | Parameter set address 2 | 16#3270 = 12912 | 16#2063/D | 16#A1/01/71 = 161/01/113 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 241
AD03 | Parameter set address 3 | 16#3271 = 12913 | 16#2063/E | 16#A1/01/72 = 161/01/114 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 242
AD04 | Parameter set address 4 | 16#3272 = 12914 | 16#2063/F | 16#A1/01/73 = 161/01/115 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 243
AD05 | Parameter set address 5 | 16#3273 = 12915 | 16#2063/10 | 16#A1/01/74 = 161/01/116 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 244
AD06 | Parameter set address 6 | 16#3274 = 12916 | 16#2063/11 | 16#A1/01/75 = 161/01/117 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 245
AD07 | Parameter set address 7 | 16#3275 = 12917 | 16#2063/12 | 16#A1/01/76 = 161/01/118 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 246
AD08 | Parameter set address 8 | 16#3276 = 12918 | 16#2063/13 | 16#A1/01/77 = 161/01/119 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 247
AD09 | Parameter set address 9 | 16#3277 = 12919 | 16#2063/14 | 16#A1/01/78 = 161/01/120 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 248
AD10 | Parameter set address 10 | 16#3278 = 12920 | 16#2063/15 | 16#A1/01/79 = 161/01/121 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 249
AD11 | Parameter set address 11 | 16#3279 = 12921 | 16#2063/16 | 16#A1/01/7A = 161/01/122 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 250
AD12 | Parameter set address 12 | 16#327A = 12922 | 16#2063/17 | 16#A1/01/7B = 161/01/123 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 251
AD13 | Parameter set address 13 | 16#327B = 12923 | 16#2063/18 | 16#A1/01/7C = 161/01/124 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 252
AD14 | Parameter set address 14 | 16#327C = 12924 | 16#2063/19 | 16#A1/01/7D = 161/01/125 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 253
AD15 | Parameter set address 15 | 16#327D = 12925 | 16#2063/1A | 16#A1/01/7E = 161/01/126 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 254
S101 | Parameter set 1 value 1 | 16#3283 = 12931 | 16#2063/20 | 16#A1/01/84 = 161/01/132 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S101) | [Set 1] (PS1-) | 255
S102 | Parameter set 1 value 2 | 16#3284 = 12932 | 16#2063/21 | 16#A1/01/85 = 161/01/133 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S102) | [Set 1] (PS1-) | 256
S103 | Parameter set 1 value 3 | 16#3285 = 12933 | 16#2063/22 | 16#A1/01/86 = 161/01/134 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S103) | [Set 1] (PS1-) | 257
S104 | Parameter set 1 value 4 | 16#3286 = 12934 | 16#2063/23 | 16#A1/01/87 = 161/01/135 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S104) | [Set 1] (PS1-) | 258
S105 | Parameter set 1 value 5 | 16#3287 = 12935 | 16#2063/24 | 16#A1/01/88 = 161/01/136 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S105) | [Set 1] (PS1-) | 259
S106 | Parameter set 1 value 6 | 16#3288 = 12936 | 16#2063/25 | 16#A1/01/89 = 161/01/137 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S106) | [Set 1] (PS1-) | 260
S107 | Parameter set 1 value 7 | 16#3289 = 12937 | 16#2063/26 | 16#A1/01/8A = 161/01/138 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S107) | [Set 1] (PS1-) | 261
S108 | Parameter set 1 value 8 | 16#328A = 12938 | 16#2063/27 | 16#A1/01/8B = 161/01/139 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S108) | [Set 1] (PS1-) | 262
S109 | Parameter set 1 value 9 | 16#328B = 12939 | 16#2063/28 | 16#A1/01/8C = 161/01/140 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S109) | [Set 1] (PS1-) | 263
S110 | Parameter set 1 value 10 | 16#328C = 12940 | 16#2063/29 | 16#A1/01/8D = 161/01/141 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S110) | [Set 1] (PS1-) | 264
S111 | Parameter set 1 value 11 | 16#328D = 12941 | 16#2063/2A | 16#A1/01/8E = 161/01/142 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S111) | [Set 1] (PS1-) | 265
S112 | Parameter set 1 value 12 | 16#328E = 12942 | 16#2063/2B | 16#A1/01/8F = 161/01/143 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S112) | [Set 1] (PS1-) | 266
S113 | Parameter set 1 value 13 | 16#328F = 12943 | 16#2063/2C | 16#A1/01/90 = 161/01/144 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S113) | [Set 1] (PS1-) | 267
S114 | Parameter set 1 value 14 | 16#3290 = 12944 | 16#2063/2D | 16#A1/01/91 = 161/01/145 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S114) | [Set 1] (PS1-) | 268
S115 | Parameter set 1 value 15 | 16#3291 = 12945 | 16#2063/2E | 16#A1/01/92 = 161/01/146 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S115) | [Set 1] (PS1-) | 269
S201 | Parameter set 2 value 1 | 16#3297 = 12951 | 16#2063/34 | 16#A1/01/98 = 161/01/152 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S201) | [Set 2] (PS2-) | 270
S202 | Parameter set 2 value 2 | 16#3298 = 12952 | 16#2063/35 | 16#A1/01/99 = 161/01/153 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S202) | [Set 2] (PS2-) | 271
S203 | Parameter set 2 value 3 | 16#3299 = 12953 | 16#2063/36 | 16#A1/01/9A = 161/01/154 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S203) | [Set 2] (PS2-) | 272
S204 | Parameter set 2 value 4 | 16#329A = 12954 | 16#2063/37 | 16#A1/01/9B = 161/01/155 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S204) | [Set 2] (PS2-) | 273
S205 | Parameter set 2 value 5 | 16#329B = 12955 | 16#2063/38 | 16#A1/01/9C = 161/01/156 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S205) | [Set 2] (PS2-) | 274
S206 | Parameter set 2 value 6 | 16#329C = 12956 | 16#2063/39 | 16#A1/01/9D = 161/01/157 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S206) | [Set 2] (PS2-) | 275
S207 | Parameter set 2 value 7 | 16#329D = 12957 | 16#2063/3A | 16#A1/01/9E = 161/01/158 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S207) | [Set 2] (PS2-) | 276
S208 | Parameter set 2 value 8 | 16#329E = 12958 | 16#2063/3B | 16#A1/01/9F = 161/01/159 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S208) | [Set 2] (PS2-) | 277
S209 | Parameter set 2 value 9 | 16#329F = 12959 | 16#2063/3C | 16#A1/01/A0 = 161/01/160 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S209) | [Set 2] (PS2-) | 278
S210 | Parameter set 2 value 10 | 16#32A0 = 12960 | 16#2063/3D | 16#A1/01/A1 = 161/01/161 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S210) | [Set 2] (PS2-) | 279
S211 | Parameter set 2 value 11 | 16#32A1 = 12961 | 16#2063/3E | 16#A1/01/A2 = 161/01/162 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S211) | [Set 2] (PS2-) | 280
S212 | Parameter set 2 value 12 | 16#32A2 = 12962 | 16#2063/3F | 16#A1/01/A3 = 161/01/163 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S212) | [Set 2] (PS2-) | 281
S213 | Parameter set 2 value 13 | 16#32A3 = 12963 | 16#2063/40 | 16#A1/01/A4 = 161/01/164 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S213) | [Set 2] (PS2-) | 282
S214 | Parameter set 2 value 14 | 16#32A4 = 12964 | 16#2063/41 | 16#A1/01/A5 = 161/01/165 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S214) | [Set 2] (PS2-) | 283
S215 | Parameter set 2 value 15 | 16#32A5 = 12965 | 16#2063/42 | 16#A1/01/A6 = 161/01/166 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S215) | [Set 2] (PS2-) | 284
S301 | Parameter set 3 value 1 | 16#32AB = 12971 | 16#2063/48 | 16#A1/01/AC = 161/01/172 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S301) | [Set 3] (PS3-) | 285
S302 | Parameter set 3 value 2 | 16#32AC = 12972 | 16#2063/49 | 16#A1/01/AD = 161/01/173 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S302) | [Set 3] (PS3-) | 286
S303 | Parameter set 3 value 3 | 16#32AD = 12973 | 16#2063/4A | 16#A1/01/AE = 161/01/174 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S303) | [Set 3] (PS3-) | 287
S304 | Parameter set 3 value 4 | 16#32AE = 12974 | 16#2063/4B | 16#A1/01/AF = 161/01/175 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S304) | [Set 3] (PS3-) | 288
S305 | Parameter set 3 value 5 | 16#32AF = 12975 | 16#2063/4C | 16#A1/01/B0 = 161/01/176 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S305) | [Set 3] (PS3-) | 289
S306 | Parameter set 3 value 6 | 16#32B0 = 12976 | 16#2063/4D | 16#A1/01/B1 = 161/01/177 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S306) | [Set 3] (PS3-) | 290
S307 | Parameter set 3 value 7 | 16#32B1 = 12977 | 16#2063/4E | 16#A1/01/B2 = 161/01/178 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S307) | [Set 3] (PS3-) | 291
S308 | Parameter set 3 value 8 | 16#32B2 = 12978 | 16#2063/4F | 16#A1/01/B3 = 161/01/179 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S308) | [Set 3] (PS3-) | 292
S309 | Parameter set 3 value 9 | 16#32B3 = 12979 | 16#2063/50 | 16#A1/01/B4 = 161/01/180 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S309) | [Set 3] (PS3-) | 293
S310 | Parameter set 3 value 10 | 16#32B4 = 12980 | 16#2063/51 | 16#A1/01/B5 = 161/01/181 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S310) | [Set 3] (PS3-) | 294
S311 | Parameter set 3 value 11 | 16#32B5 = 12981 | 16#2063/52 | 16#A1/01/B6 = 161/01/182 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S311) | [Set 3] (PS3-) | 295
S312 | Parameter set 3 value 12 | 16#32B6 = 12982 | 16#2063/53 | 16#A1/01/B7 = 161/01/183 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S312) | [Set 3] (PS3-) | 296
S313 | Parameter set 3 value 13 | 16#32B7 = 12983 | 16#2063/54 | 16#A1/01/B8 = 161/01/184 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S313) | [Set 3] (PS3-) | 297
S314 | Parameter set 3 value 14 | 16#32B8 = 12984 | 16#2063/55 | 16#A1/01/B9 = 161/01/185 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S314) | [Set 3] (PS3-) | 298
S315 | Parameter set 3 value 15 | 16#32B9 = 12985 | 16#2063/56 | 16#A1/01/BA = 161/01/186 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S315) | [Set 3] (PS3-) | 299
LSP | Low Speed | 16#0C21 = 3105 | 16#2001/6 | 16#70/01/6A = 112/01/106 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0 | 0.0 Hz ... 500.0 Hz | [Low Speed] (LSP) | [Speed Limits] (SLM-) [Simply start] (SIM-) [Settings] (SEt-) [Pump start stop] (PSt-) | 300
HSP | High Speed | 16#0C20 = 3104 | 16#2001/5 | 16#70/01/69 = 112/01/105 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0.0 Hz ... 500.0 Hz | [High Speed] (HSP) | [Speed Limits] (SLM-) [Simply start] (SIM-) [Settings] (SEt-) [Pump start stop] (PSt-) | 301
ITH | Motor Th Current | 16#2596 = 9622 | 16#2042/17 | 16#91/01/17 = 145/01/23 | - | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | 0 ... 65535 | [Motor Th Current] (ItH) | [Motor thermal monit] (tHt-) [Simply start] (SIM-) [Motor monitoring] (MOP-) [Settings] (SEt-) | 302
SPGU | Inertia Factor | 16#259D = 9629 | 16#2042/1E | 16#91/01/1E = 145/01/30 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 40 % | 0 % ... 1000 % | [Inertia Factor] (SPGU) | [Motor control] (drC-) [Settings] (SEt-) | 303
SPG | Speed prop. gain | 16#238F = 9103 | 16#203D/4 | 16#8E/01/68 = 142/01/104 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 40 % | 0 % ... 1000 % | [Speed prop. gain] (SPG) | [Settings] (SEt-) | 304
SIT | Speed time integral | 16#2390 = 9104 | 16#203D/5 | 16#8E/01/69 = 142/01/105 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | (call SIT_DefaultValue_functionCaliber []) | 1 ms ... 65535 ms | [Speed time integral] (SIt) | [Settings] (SEt-) | 305
SFC | K speed loop filter | 16#2391 = 9105 | 16#203D/6 | 16#8E/01/6A = 142/01/106 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 65 | 0 ... 100 | [K speed loop filter] (SFC) | [Settings] (SEt-) | 306
FFH | Spd est. filter time | 16#239B = 9115 | 16#203D/10 | 16#8E/01/74 = 142/01/116 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 ms | Depends of rating | 0.0 ms ... 100.0 ms |  |  | 307
CRTF | Current Filter Time | 16#239C = 9116 | 16#203D/11 | 16#8E/01/75 = 142/01/117 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 ms | [Auto] (AUtO) | [Auto] (AUtO) ... 100.0 ms | [Current Filter Time] (CrtF) | [data] (Mtd-) | 308
CTD | High Current Thd | 16#2AF9 = 11001 | 16#2050/2 | 16#98/01/02 = 152/01/02 | - | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | INV | Depends of rating | [High Current Thd] (Ctd) | [Threshold reached] (tHrE-) [Settings] (SEt-) | 309
TTH | High torque thd. | 16#2B08 = 11016 | 16#2050/11 | 16#98/01/11 = 152/01/17 | - | Configuration and settings | R/W | INT (Signed16) | 1 % | 100 % | -300 % ... 300 % | [High torque thd.] (ttH) | [Threshold reached] (tHrE-) [Settings] (SEt-) | 310
TTL | Low torque thd. | 16#2B07 = 11015 | 16#2050/10 | 16#98/01/10 = 152/01/16 | - | Configuration and settings | R/W | INT (Signed16) | 1 % | 50 % | -300 % ... 300 % | [Low torque thd.] (ttL) | [Threshold reached] (tHrE-) [Settings] (SEt-) | 311
FTD | Motor Freq Thd | 16#2AFB = 11003 | 16#2050/4 | 16#98/01/04 = 152/01/04 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0.0 Hz ... 500.0 Hz | [Motor Freq Thd] (Ftd) | [Threshold reached] (tHrE-) [Settings] (SEt-) | 312
F2D | Freq. threshold 2 | 16#2AFC = 11004 | 16#2050/5 | 16#98/01/05 = 152/01/05 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0.0 Hz ... 500.0 Hz | [Freq. threshold 2] (F2d) | [Threshold reached] (tHrE-) [Settings] (SEt-) | 313
JF2 | Skip Frequency 2 | 16#2C26 = 11302 | 16#2053/3 | 16#99/01/67 = 153/01/103 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 500.0 Hz | [Skip Frequency 2] (JF2) | [Jump frequency] (JUF-) [Settings] (SEt-) | 314
JPF | Skip Frequency | 16#2C25 = 11301 | 16#2053/2 | 16#99/01/66 = 153/01/102 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 500.0 Hz | [Skip Frequency] (JPF) | [Jump frequency] (JUF-) [Settings] (SEt-) | 315
JFH | Skip Freq.Hysteresis | 16#2C2F = 11311 | 16#2053/C | 16#99/01/70 = 153/01/112 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 1.0 Hz | 0.1 Hz ... 10.0 Hz | [Skip Freq.Hysteresis] (JFH) | [Jump frequency] (JUF-) [Settings] (SEt-) | 316
JF3 | 3rd Skip Frequency | 16#2C27 = 11303 | 16#2053/4 | 16#99/01/68 = 153/01/104 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 500.0 Hz | [3rd Skip Frequency] (JF3) | [Jump frequency] (JUF-) [Settings] (SEt-) | 317
BFR | Motor Standard | 16#0BC7 = 3015 | 16#2000/10 | 16#70/01/10 = 112/01/16 | BFR | Configuration and settings | R/WS | WORD (Enumeration) | - | [50Hz IEC] (50) | - | [Motor Standard] (bFr) | [Simply start] (SIM-) [data] (Mtd-) | 318
NPR | Nominal Motor Power | 16#258D = 9613 | 16#2042/E | 16#91/01/0E = 145/01/14 | - | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | Depends of rating | 0 ... 65535 | [Nominal Motor Power] (nPr) | [Simply start] (SIM-) [data] (Mtd-) | 319
COS | Motor 1 Cosinus Phi | 16#2586 = 9606 | 16#2042/7 | 16#91/01/07 = 145/01/07 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 | Depends of rating | 0.50 ... 1.00 | [Motor 1 Cosinus Phi] (COS) | [Simply start] (SIM-) [data] (Mtd-) | 320
UNS | Nom Motor Voltage | 16#2581 = 9601 | 16#2042/2 | 16#91/01/02 = 145/01/02 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | Depends of rating | 100 V ... 690 V | [Nom Motor Voltage] (UnS) | [Simply start] (SIM-) [data] (Mtd-) | 321
NCR | Nom Motor Current | 16#2583 = 9603 | 16#2042/4 | 16#91/01/04 = 145/01/04 | - | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | Depends of rating | 0 ... 65535 | [Nom Motor Current] (nCr) | [Simply start] (SIM-) [data] (Mtd-) | 322
FRS | Nominal Motor Freq | 16#2582 = 9602 | 16#2042/3 | 16#91/01/03 = 145/01/03 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 40.0 Hz ... 500.0 Hz | [Nominal Motor Freq] (FrS) | [Simply start] (SIM-) [data] (Mtd-) | 323
NSP | Nominal Motor Speed | 16#2584 = 9604 | 16#2042/5 | 16#91/01/05 = 145/01/05 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 rpm | Depends of rating | 0 rpm ... 65535 rpm | [Nominal Motor Speed] (nSP) | [Simply start] (SIM-) [data] (Mtd-) | 324
TFR | Max Frequency | 16#0C1F = 3103 | 16#2001/4 | 16#70/01/68 = 112/01/104 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 10.0 Hz ... 500.0 Hz | [Max Frequency] (tFr) | [Simply start] (SIM-) | 325
TUN | Autotuning | 16#2588 = 9608 | 16#2042/9 | 16#91/01/09 = 145/01/09 | ACTION | Configuration and settings | R/W | WORD (Enumeration) | - | [No action] (nO) | - | [Autotuning] (tUn) | [Simply start] (SIM-) [Motor tune] (MtU-) | 326
AUT | Automatic autotune | 16#258F = 9615 | 16#2042/10 | 16#91/01/10 = 145/01/16 | AUT | Configuration and settings | R/W | WORD (Enumeration) | - | [No] (nO) | - | [Automatic autotune] (AUt) | [Motor tune] (MtU-) | 327
TUS | Autotuning Status | 16#2589 = 9609 | 16#2042/A | 16#91/01/0A = 145/01/10 | ACT | Configuration and settings | [always] | WORD (Enumeration) | - | [Not Done] (tAb) | - | [Autotuning Status] (tUS) | [Simply start] (SIM-) [Motor tune] (MtU-) | 328
CTT | Motor control type | 16#2587 = 9607 | 16#2042/8 | 16#91/01/08 = 145/01/08 | CTT | Configuration and settings | R/WS | WORD (Enumeration) | - | [U/F VC Quad.] (UFq) | - | [Motor control type] (Ctt) | [Motor parameters] (MPA-) | 329
U1 | U1 | 16#3073 = 12403 | 16#205E/4 | 16#9F/01/04 = 159/01/04 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | 0 V | 0 V ... 800 V | [U1] (U1) | [Motor control] (drC-) | 330
F1 | F1 | 16#3074 = 12404 | 16#205E/5 | 16#9F/01/05 = 159/01/05 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 500.0 Hz | [F1] (F1) | [Motor control] (drC-) | 331
U2 | U2 | 16#3075 = 12405 | 16#205E/6 | 16#9F/01/06 = 159/01/06 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | 0 V | 0 V ... 800 V | [U2] (U2) | [Motor control] (drC-) | 332
F2 | F2 | 16#3076 = 12406 | 16#205E/7 | 16#9F/01/07 = 159/01/07 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 500.0 Hz | [F2] (F2) | [Motor control] (drC-) | 333
U3 | U3 | 16#3077 = 12407 | 16#205E/8 | 16#9F/01/08 = 159/01/08 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | 0 V | 0 V ... 800 V | [U3] (U3) | [Motor control] (drC-) | 334
F3 | F3 | 16#3078 = 12408 | 16#205E/9 | 16#9F/01/09 = 159/01/09 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 500.0 Hz | [F3] (F3) | [Motor control] (drC-) | 335
U4 | U4 | 16#3079 = 12409 | 16#205E/A | 16#9F/01/0A = 159/01/10 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | 0 V | 0 V ... 800 V | [U4] (U4) | [Motor control] (drC-) | 336
F4 | F4 | 16#307A = 12410 | 16#205E/B | 16#9F/01/0B = 159/01/11 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 500.0 Hz | [F4] (F4) | [Motor control] (drC-) | 337
U5 | U5 | 16#307B = 12411 | 16#205E/C | 16#9F/01/0C = 159/01/12 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | 0 V | 0 V ... 800 V | [U5] (U5) | [Motor control] (drC-) | 338
F5 | F5 | 16#307C = 12412 | 16#205E/D | 16#9F/01/0D = 159/01/13 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 500.0 Hz | [F5] (F5) | [Motor control] (drC-) | 339
NCRS | Sync Nominal I | 16#25C6 = 9670 | 16#2042/47 | 16#91/01/47 = 145/01/71 | - | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | Depends of rating | 0 ... 65535 | [Sync Nominal I] (nCrS) | [data] (Mtd-) | 340
NSPS | Nom SyncMotor Speed | 16#25C7 = 9671 | 16#2042/48 | 16#91/01/48 = 145/01/72 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 rpm | Depends of rating | 0 rpm ... 65535 rpm | [Nom SyncMotor Speed] (nSPS) | [data] (Mtd-) | 341
PPNS | Pole pairs | 16#25C8 = 9672 | 16#2042/49 | 16#91/01/49 = 145/01/73 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | Depends of rating | 1 ... 50 | [Pole pairs] (PPnS) | [data] (Mtd-) | 342
TQS | Nom Motor torque | 16#25D4 = 9684 | 16#2042/55 | 16#91/01/55 = 145/01/85 | - | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | Depends of rating | Depends of rating | [Nom Motor torque] (tqS) | [data] (Mtd-) | 343
PHS | Syn. EMF constant | 16#25C9 = 9673 | 16#2042/4A | 16#91/01/4A = 145/01/74 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mV/rpm | 0.0 mV/rpm | 0.0 mV/rpm ... 6553.5 mV/rpm | [Syn. EMF constant] (PHS) | [data] (Mtd-) | 344
LDS | Autotune L d-axis | 16#25CA = 9674 | 16#2042/4B | 16#91/01/4B = 145/01/75 | - | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | Depends of rating | Depends of rating | [Autotune L d-axis] (LdS) | [data] (Mtd-) | 345
LQS | Autotune L q-axis | 16#25CB = 9675 | 16#2042/4C | 16#91/01/4C = 145/01/76 | - | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | Depends of rating | Depends of rating | [Autotune L q-axis] (LqS) | [data] (Mtd-) | 346
RSAS | SyncMotor Stator R | 16#25D2 = 9682 | 16#2042/53 | 16#91/01/53 = 145/01/83 | - | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | Depends of rating | Depends of rating | [SyncMotor Stator R] (rSAS) | [data] (Mtd-) | 347
UFR | IR compensation | 16#2597 = 9623 | 16#2042/18 | 16#91/01/18 = 145/01/24 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 100 % | 0 % ... 200 % | [IR compensation] (UFr) | [Motor control] (drC-) [Settings] (SEt-) | 348
SLP | Slip compensation | 16#2599 = 9625 | 16#2042/1A | 16#91/01/1A = 145/01/26 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | Refer to programming manual | 0 % ... 300 % | [Slip compensation] (SLP) | [Motor control] (drC-) [Settings] (SEt-) | 349
PPN | Number of pairs of poles calculated | 16#2592 = 9618 | 16#2042/13 | 16#91/01/13 = 145/01/19 | - | Configuration and settings | [gatingOff] | UINT (Unsigned16) | 1 | Depends of rating | 1 ... 100 | (PPn) | [data] (Mtd-) | 350
RSA | AsyncMotor R Stator | 16#25AA = 9642 | 16#2042/2B | 16#91/01/2B = 145/01/43 | - | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | Depends of rating | Depends of rating | [AsyncMotor R Stator] (rSA) | [data] (Mtd-) | 351
IDA | Magnetizing Current | 16#25B4 = 9652 | 16#2042/35 | 16#91/01/35 = 145/01/53 | - | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | Depends of rating | Depends of rating | [Magnetizing Current] (IdA) | [data] (Mtd-) | 352
LFA | AsyncMotor Lf Induct | 16#25BE = 9662 | 16#2042/3F | 16#91/01/3F = 145/01/63 | - | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | Depends of rating | Depends of rating | [AsyncMotor Lf Induct] (LFA) | [data] (Mtd-) | 353
TRA | Rotor Time Const | 16#25C3 = 9667 | 16#2042/44 | 16#91/01/44 = 145/01/68 | - | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | Depends of rating | Depends of rating | [Rotor Time Const] (trA) | [data] (Mtd-) | 354
FRSS | Sync Nominal Freq | 16#25CF = 9679 | 16#2042/50 | 16#91/01/50 = 145/01/80 | - | Configuration and settings | [always] | UINT (Unsigned16) | 0.1 Hz | (NSPS * PPNS / 6) | 10.0 Hz ... 500.0 Hz | [Sync Nominal Freq] (FrSS) | [data] (Mtd-) | 355
SFR | Switching frequency | 16#0C1E = 3102 | 16#2001/3 | 16#70/01/67 = 112/01/103 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 kHz | @EP@ | 1.0 kHz ... 16.0 kHz | [Switching frequency] (SFr) | [Switching frequency] (SWF-) [Settings] (SEt-) | 356
CLI | Current Limitation | 16#23F1 = 9201 | 16#203E/2 | 16#8F/01/02 = 143/01/02 | - | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | (INV * 11 / 10) | Depends of rating | [Current Limitation] (CLI) | [Motor monitoring] (MOP-) [Settings] (SEt-) | 357
SFT | Switch Freq Type | 16#0C1D = 3101 | 16#2001/2 | 16#70/01/66 = 112/01/102 | SFT | Configuration and settings | R/WS | WORD (Enumeration) | - | [SFR type 1] (HF1) | - | [Switch Freq Type] (SFt) | [Switching frequency] (SWF-) | 358
NRD | Noise Reduction | 16#0C23 = 3107 | 16#2001/8 | 16#70/01/6C = 112/01/108 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Noise Reduction] (nrd) | [Switching frequency] (SWF-) | 359
BOA | Boost activation | 16#3656 = 13910 | 16#206D/B | 16#A6/01/6F = 166/01/111 | BOA | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual | - | [Boost activation] (bOA) | [Motor control] (drC-) | 360
SVL | Motor surge limit. | 16#3139 = 12601 | 16#2060/2 | 16#A0/01/02 = 160/01/02 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Motor surge limit.] (SUL) | [Switching frequency] (SWF-) | 361
SOP | Attenuation Time | 16#313A = 12602 | 16#2060/3 | 16#A0/01/03 = 160/01/03 | SOP | Configuration and settings | R/WS | WORD (Enumeration) | - | [8 ms] (8) | - | [Attenuation Time] (SOP) | [Motor monitoring] (MOP-) [Switching frequency] (SWF-) | 362
FFM | Fan mode | 16#0C3A = 3130 | 16#2001/1F | 16#70/01/83 = 112/01/131 | FFM | Configuration and settings | R/W | WORD (Enumeration) | - | [Standard] (Std) | - | [Fan mode] (FFM) | [Settings] (SEt-) [Fan management] (FAMA-) | 363
TCC | 2/3-Wire Control | 16#2B5D = 11101 | 16#2051/2 | 16#98/01/66 = 152/01/102 | TCC | Configuration and settings | R/WS | WORD (Enumeration) | - | [2-Wire Control] (2C) | - | [2/3-Wire Control] (tCC) | [Command and Reference] (CrP-) [Simply start] (SIM-) | 364
TCT | 2-wire type | 16#2B5E = 11102 | 16#2051/3 | 16#98/01/67 = 152/01/103 | TCT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Transition] (trn) | - | [2-wire type] (tCt) | [Command and Reference] (CrP-) | 365
RRS | Reverse Assign | 16#2B61 = 11105 | 16#2051/6 | 16#98/01/6A = 152/01/106 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | "NO" | - | [Reverse Assign] (rrS) | [Command and Reference] (CrP-) | 366
BSP | Ref Freq template | 16#0C22 = 3106 | 16#2001/7 | 16#70/01/6B = 112/01/107 | BSP | Configuration and settings | R/W | WORD (Enumeration) | - | [Standard] (bSd) | - | [Ref Freq template] (bSP) | [Speed Limits] (SLM-) [Pump start stop] (PSt-) [Input/Output] (IO-) | 367
AI1T | AI1 Type | 16#1132 = 4402 | 16#200E/3 | 16#77/01/03 = 119/01/03 | AIOT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Voltage] (10U) | - | [AI1 Type] (AI1t) | [Feedback] (Fdb-) | 368
UIL1 | AI1 Min. Value | 16#113C = 4412 | 16#200E/D | 16#77/01/0D = 119/01/13 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 0.0 V | 0.0 V ... 10.0 V | [AI1 Min. Value] (UIL1) | [Feedback] (Fdb-) | 369
UIH1 | AI1 Max Value | 16#1146 = 4422 | 16#200E/17 | 16#77/01/17 = 119/01/23 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 10.0 V | 0.0 V ... 10.0 V | [AI1 Max Value] (UIH1) | [Feedback] (Fdb-) | 370
AI1F | AI1 filter | 16#1164 = 4452 | 16#200E/35 | 16#77/01/35 = 119/01/53 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 10.00 s | [AI1 filter] (AI1F) | [AI1 configuration] (AI1-) | 371
AI1E | AI1 Interm. point X | 16#116E = 4462 | 16#200E/3F | 16#77/01/3F = 119/01/63 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [AI1 Interm. point X] (AI1E) | [AI1 configuration] (AI1-) | 372
AI1S | AI1 Interm. point Y | 16#1178 = 4472 | 16#200E/49 | 16#77/01/49 = 119/01/73 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [AI1 Interm. point Y] (AI1S) | [AI1 configuration] (AI1-) | 373
AI2T | AI2 Type | 16#1133 = 4403 | 16#200E/4 | 16#77/01/04 = 119/01/04 | AIOT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Voltage] (10U) | - | [AI2 Type] (AI2t) | [Feedback] (Fdb-) | 374
UIL2 | AI2 Min. Value | 16#113D = 4413 | 16#200E/E | 16#77/01/0E = 119/01/14 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 0.0 V | 0.0 V ... 10.0 V | [AI2 Min. Value] (UIL2) | [Feedback] (Fdb-) | 375
UIH2 | AI2 Max value | 16#1147 = 4423 | 16#200E/18 | 16#77/01/18 = 119/01/24 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 10.0 V | 0.0 V ... 10.0 V | [AI2 Max value] (UIH2) | [Feedback] (Fdb-) | 376
AI2F | AI2 filter | 16#1165 = 4453 | 16#200E/36 | 16#77/01/36 = 119/01/54 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 10.00 s | [AI2 filter] (AI2F) | [AI2 configuration] (AI2-) | 377
AI2E | AI2 Interm. point X | 16#116F = 4463 | 16#200E/40 | 16#77/01/40 = 119/01/64 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [AI2 Interm. point X] (AI2E) | [AI2 configuration] (AI2-) | 378
AI2S | AI2 Interm. point Y | 16#1179 = 4473 | 16#200E/4A | 16#77/01/4A = 119/01/74 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [AI2 Interm. point Y] (AI2S) | [AI2 configuration] (AI2-) | 379
AI3T | AI3 Type | 16#1134 = 4404 | 16#200E/5 | 16#77/01/05 = 119/01/05 | AIOT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Current] (0A) | - | [AI3 Type] (AI3t) | [Feedback] (Fdb-) | 380
CRL3 | AI3 Min. Value | 16#1152 = 4434 | 16#200E/23 | 16#77/01/23 = 119/01/35 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mA | 0.0 mA | 0.0 mA ... 20.0 mA | [AI3 Min. Value] (CrL3) | [Feedback] (Fdb-) | 381
CRH3 | AI3 Max Value | 16#115C = 4444 | 16#200E/2D | 16#77/01/2D = 119/01/45 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mA | 20.0 mA | 0.0 mA ... 20.0 mA | [AI3 Max Value] (CrH3) | [Feedback] (Fdb-) | 382
AI3F | AI3 filter | 16#1166 = 4454 | 16#200E/37 | 16#77/01/37 = 119/01/55 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 10.00 s | [AI3 filter] (AI3F) | [AI3 configuration] (AI3-) | 383
AI3E | AI3 X Interm. point | 16#1170 = 4464 | 16#200E/41 | 16#77/01/41 = 119/01/65 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [AI3 X Interm. point] (AI3E) | [AI3 configuration] (AI3-) | 384
AI3S | AI3 Y Interm. point | 16#117A = 4474 | 16#200E/4B | 16#77/01/4B = 119/01/75 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [AI3 Y Interm. point] (AI3S) | [AI3 configuration] (AI3-) | 385
AO1 | AQ1 assignment | 16#139D = 5021 | 16#2014/16 | 16#7A/01/16 = 122/01/22 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Motor Frequency] (OFr) | - | [AQ1 assignment] (AO1) | [AQ1 configuration] (AO1-) | 386
AO1T | AQ1 Type | 16#11F9 = 4601 | 16#2010/2 | 16#78/01/02 = 120/01/02 | AIOT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Current] (0A) | - | [AQ1 Type] (AO1t) | [AQ1 configuration] (AO1-) | 387
AOL1 | AQ1 min output | 16#1221 = 4641 | 16#2010/2A | 16#78/01/2A = 120/01/42 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mA | 0.0 mA | 0.0 mA ... 20.0 mA | [AQ1 min output] (AOL1) | [AQ1 configuration] (AO1-) | 388
AOH1 | AQ1 max output | 16#122B = 4651 | 16#2010/34 | 16#78/01/34 = 120/01/52 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mA | 20.0 mA | 0.0 mA ... 20.0 mA | [AQ1 max output] (AOH1) | [AQ1 configuration] (AO1-) | 389
UOL1 | AQ1 min Output | 16#120D = 4621 | 16#2010/16 | 16#78/01/16 = 120/01/22 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 0.0 V | 0.0 V ... 10.0 V | [AQ1 min Output] (UOL1) | [AQ1 configuration] (AO1-) | 390
UOH1 | AQ1 max Output | 16#1217 = 4631 | 16#2010/20 | 16#78/01/20 = 120/01/32 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 10.0 V | 0.0 V ... 10.0 V | [AQ1 max Output] (UOH1) | [AQ1 configuration] (AO1-) | 391
ASL1 | Scaling AQ1 min | 16#1235 = 4661 | 16#2010/3E | 16#78/01/3E = 120/01/62 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 % | 0.0 % | 0.0 % ... 100.0 % | [Scaling AQ1 min] (ASL1) | [AQ1 configuration] (AO1-) | 392
ASH1 | Scaling AQ1 max | 16#123F = 4671 | 16#2010/48 | 16#78/01/48 = 120/01/72 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 % | 100.0 % | 0.0 % ... 100.0 % | [Scaling AQ1 max] (ASH1) | [AQ1 configuration] (AO1-) | 393
AO1F | AQ1 Filter | 16#1203 = 4611 | 16#2010/C | 16#78/01/0C = 120/01/12 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 10.00 s | [AQ1 Filter] (AO1F) | [AQ1 configuration] (AO1-) | 394
FR1 | Ref Freq 1 Config | 16#20DD = 8413 | 16#2036/E | 16#8B/01/0E = 139/01/14 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | "AI1" | - | [Ref Freq 1 Config] (Fr1) | [Command and Reference] (CrP-) | 395
RIN | Reverse Disable | 16#0C24 = 3108 | 16#2001/9 | 16#70/01/6D = 112/01/109 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [Yes] (YES) | - | [Reverse Disable] (rIn) | [Command and Reference] (CrP-) [Reverse disable] (rEIn-) | 396
PST | Stop Key Enable | 16#FA02 = 64002 |  | = | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [Yes] (YES) | - | [Stop Key Enable] (PSt) | [Command and Reference] (CrP-) | 397
CHCF | Control Mode | 16#20D1 = 8401 | 16#2036/2 | 16#8B/01/02 = 139/01/02 | CHCF | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not separ.] (SIM) | - | [Control Mode] (CHCF) | [Command and Reference] (CrP-) | 398
CCS | Command Switching | 16#20E5 = 8421 | 16#2036/16 | 16#8B/01/16 = 139/01/22 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Cmd Channel 1] (Cd1) | - | [Command Switching] (CCS) | [Command and Reference] (CrP-) | 399
CD1 | Cmd channel 1 | 16#20E7 = 8423 | 16#2036/18 | 16#8B/01/18 = 139/01/24 | CDX | Configuration and settings | R/WS | WORD (Enumeration) | - | [Terminals] (tEr) | - | [Cmd channel 1] (Cd1) | [Command and Reference] (CrP-) | 400
CD2 | Cmd channel 2 | 16#20E8 = 8424 | 16#2036/19 | 16#8B/01/19 = 139/01/25 | CDX | Configuration and settings | R/WS | WORD (Enumeration) | - | [Modbus] (Mdb) | - | [Cmd channel 2] (Cd2) | [Command and Reference] (CrP-) | 401
RFC | Freq Switch Assign | 16#20DB = 8411 | 16#2036/C | 16#8B/01/0C = 139/01/12 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | "FR1" | - | [Freq Switch Assign] (rFC) | [Command and Reference] (CrP-) | 402
FR2 | Ref Freq 2 Config | 16#20DE = 8414 | 16#2036/F | 16#8B/01/0F = 139/01/15 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | "NO" | - | [Ref Freq 2 Config] (Fr2) | [Command and Reference] (CrP-) | 403
COP | Copy Ch1-Ch2 | 16#20D2 = 8402 | 16#2036/3 | 16#8B/01/03 = 139/01/03 | COP | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Copy Ch1-Ch2] (COP) | [Command and Reference] (CrP-) | 404
FN1 | F1 key assignment | 16#34BD = 13501 | 16#2069/2 | 16#A4/01/66 = 164/01/102 | CSLFN | Configuration and settings | R/WS | WORD (Enumeration) | - |  | - | [F1 key assignment] (Fn1) | [Functions key mgnt] (F G-) | 405
FN2 | F2 key assignment | 16#34BE = 13502 | 16#2069/3 | 16#A4/01/67 = 164/01/103 | CSLFN | Configuration and settings | R/WS | WORD (Enumeration) | - |  | - | [F2 key assignment] (Fn2) | [Functions key mgnt] (F G-) | 406
FN3 | F3 key assignment | 16#34BF = 13503 | 16#2069/4 | 16#A4/01/68 = 164/01/104 | CSLFN | Configuration and settings | R/WS | WORD (Enumeration) | - |  | - | [F3 key assignment] (Fn3) | [Functions key mgnt] (F G-) | 407
FN4 | F4 key assignment | 16#34C0 = 13504 | 16#2069/5 | 16#A4/01/69 = 164/01/105 | CSLFN | Configuration and settings | R/WS | WORD (Enumeration) | - |  | - | [F4 key assignment] (Fn4) | [Functions key mgnt] (F G-) | 408
BMP | HMI cmd. | 16#34D9 = 13529 | 16#2069/1E | 16#A4/01/82 = 164/01/130 | BMP | Configuration and settings | R/WS | WORD (Enumeration) | - | [Disabled] (dIS) | - | [HMI cmd.] (bMP) | [Command and Reference] (CrP-) | 409
RCB | Ref 1B switching | 16#20DC = 8412 | 16#2036/D | 16#8B/01/0D = 139/01/13 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ref Freq Channel 1] (Fr1) | - | [Ref 1B switching] (rCb) | [Command and Reference] (CrP-) | 410
FR1B | Ref.1B channel | 16#20DF = 8415 | 16#2036/10 | 16#8B/01/10 = 139/01/16 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Configured] (nO) | - | [Ref.1B channel] (Fr1b) | [Command and Reference] (CrP-) | 411
SA2 | Summing Input 2 | 16#2E19 = 11801 | 16#2058/2 | 16#9C/01/02 = 156/01/02 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | "NO" | - | [Summing Input 2] (SA2) | [Ref. operations] (OAI-) | 412
SA3 | Summing Input 3 | 16#2E1A = 11802 | 16#2058/3 | 16#9C/01/03 = 156/01/03 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Configured] (nO) | - | [Summing Input 3] (SA3) | [Ref. operations] (OAI-) | 413
DA2 | Subtract Ref Freq 2 | 16#2E23 = 11811 | 16#2058/C | 16#9C/01/0C = 156/01/12 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Configured] (nO) | - | [Subtract Ref Freq 2] (dA2) | [Ref. operations] (OAI-) | 414
DA3 | Subtract Ref Freq 3 | 16#2E24 = 11812 | 16#2058/D | 16#9C/01/0D = 156/01/13 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Configured] (nO) | - | [Subtract Ref Freq 3] (dA3) | [Ref. operations] (OAI-) | 415
MA2 | Ref Freq 2 Multiply | 16#2E2D = 11821 | 16#2058/16 | 16#9C/01/16 = 156/01/22 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Configured] (nO) | - | [Ref Freq 2 Multiply] (MA2) | [Ref. operations] (OAI-) | 416
MA3 | Ref Freq 3 Multiply | 16#2E2E = 11822 | 16#2058/17 | 16#9C/01/17 = 156/01/23 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Configured] (nO) | - | [Ref Freq 3 Multiply] (MA3) | [Ref. operations] (OAI-) | 417
RPT | Ramp Type | 16#232C = 9004 | 16#203C/5 | 16#8E/01/05 = 142/01/05 | RPT | Configuration and settings | R/W | WORD (Enumeration) | - | [Linear] (LIn) | - | [Ramp Type] (rPt) | [Ramp] (rAMP-) | 418
INR | Ramp increment | 16#233C = 9020 | 16#203C/15 | 16#8E/01/15 = 142/01/21 | INR | Configuration and settings | R/W | WORD (Enumeration) | - | [0.1] (0.1) | - | [Ramp increment] (Inr) | [Ramp] (rAMP-) [Settings] (SEt-) | 419
ACC | Acceleration | 16#2329 = 9001 | 16#203C/2 | 16#8E/01/02 = 142/01/02 | - | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | Refer to programming manual | [Acceleration] (ACC) | [Ramp] (rAMP-) [Simply start] (SIM-) [Settings] (SEt-) [Pump start stop] (PSt-) | 420
DEC | Deceleration | 16#232A = 9002 | 16#203C/3 | 16#8E/01/03 = 142/01/03 | - | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | Refer to programming manual | [Deceleration] (dEC) | [Ramp] (rAMP-) [Simply start] (SIM-) [Settings] (SEt-) [Pump start stop] (PSt-) | 421
TA1 | Begin Acc round | 16#232D = 9005 | 16#203C/6 | 16#8E/01/06 = 142/01/06 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 10 % | 0 % ... 100 % | [Begin Acc round] (tA1) | [Ramp] (rAMP-) [Settings] (SEt-) | 422
TA2 | End Acc round | 16#232E = 9006 | 16#203C/7 | 16#8E/01/07 = 142/01/07 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 10 % | 0 % ... 100 % | [End Acc round] (tA2) | [Ramp] (rAMP-) [Settings] (SEt-) | 423
TA3 | Begin Dec round | 16#232F = 9007 | 16#203C/8 | 16#8E/01/08 = 142/01/08 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 10 % | 0 % ... 100 % | [Begin Dec round] (tA3) | [Ramp] (rAMP-) [Settings] (SEt-) | 424
TA4 | End Dec round | 16#2330 = 9008 | 16#203C/9 | 16#8E/01/09 = 142/01/09 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 10 % | 0 % ... 100 % | [End Dec round] (tA4) | [Ramp] (rAMP-) [Settings] (SEt-) | 425
FRT | Ramp 2 Thd | 16#2333 = 9011 | 16#203C/C | 16#8E/01/0C = 142/01/12 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 500.0 Hz | [Ramp 2 Thd] (Frt) | [Ramp switching] (rPt-) | 426
RPS | Ramp Switch Assign | 16#2332 = 9010 | 16#203C/B | 16#8E/01/0B = 142/01/11 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Assigned] (nO) | - | [Ramp Switch Assign] (rPS) | [Ramp switching] (rPt-) | 427
AC2 | Acceleration 2 | 16#2334 = 9012 | 16#203C/D | 16#8E/01/0D = 142/01/13 | - | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | Refer to programming manual | [Acceleration 2] (AC2) | [Ramp switching] (rPt-) [Settings] (SEt-) | 428
DE2 | Deceleration 2 | 16#2335 = 9013 | 16#203C/E | 16#8E/01/0E = 142/01/14 | - | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | Refer to programming manual | [Deceleration 2] (dE2) | [Ramp switching] (rPt-) [Settings] (SEt-) | 429
BRA | Dec.Ramp Adapt | 16#232B = 9003 | 16#203C/4 | 16#8E/01/04 = 142/01/04 | BRA | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual | - | [Dec.Ramp Adapt] (brA) | [Ramp] (rAMP-) | 430
STT | Type of stop | 16#2BC1 = 11201 | 16#2052/2 | 16#99/01/02 = 153/01/02 | STT | Configuration and settings | R/WS | WORD (Enumeration) | - | [On Ramp] (rMP) | - | [Type of stop] (Stt) | [Stop configuration] (Stt-) | 431
FFT | Freewheel stop Thd | 16#2BD4 = 11220 | 16#2052/15 | 16#99/01/15 = 153/01/21 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | (Max (((call NominalMotorFrequency []) / 250), 2)) | 0.2 Hz ... 500.0 Hz | [Freewheel stop Thd] (FFt) | [Stop configuration] (Stt-) [Settings] (SEt-) | 432
NST | Freewheel Stop | 16#2BC2 = 11202 | 16#2052/3 | 16#99/01/03 = 153/01/03 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Assigned] (nO) | - | [Freewheel Stop] (nSt) | [Stop configuration] (Stt-) | 433
FST | Fast Stop Assign | 16#2BC4 = 11204 | 16#2052/5 | 16#99/01/05 = 153/01/05 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Assigned] (nO) | - | [Fast Stop Assign] (FSt) | [Stop configuration] (Stt-) | 434
DCF | Ramp Divider | 16#2BDE = 11230 | 16#2052/1F | 16#99/01/1F = 153/01/31 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 4 | 0 ... 10 | [Ramp Divider] (dCF) | [Stop configuration] (Stt-) [Settings] (SEt-) | 435
DCI | DC Injection Assign | 16#2BC3 = 11203 | 16#2052/4 | 16#99/01/04 = 153/01/04 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Assigned] (nO) | - | [DC Injection Assign] (dCI) | [Stop configuration] (Stt-) | 436
IDC | DC Inj Level 1 | 16#2BCA = 11210 | 16#2052/B | 16#99/01/0B = 153/01/11 | - | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | (INV * 7 / 10) | Depends of rating | [DC Inj Level 1] (IdC) | [Stop configuration] (Stt-) [Settings] (SEt-) | 437
TDI | DC Inj Time 1 | 16#2BCD = 11213 | 16#2052/E | 16#99/01/0E = 153/01/14 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.1 s ... 30.0 s | [DC Inj Time 1] (tdI) | [Stop configuration] (Stt-) [Settings] (SEt-) | 438
IDC2 | DC Inj Level 2 | 16#2BCC = 11212 | 16#2052/D | 16#99/01/0D = 153/01/13 | - | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | (INV / 2) | Depends of rating | [DC Inj Level 2] (IdC2) | [Stop configuration] (Stt-) [Settings] (SEt-) | 439
TDC | DC Inj Time 2 | 16#2BCB = 11211 | 16#2052/C | 16#99/01/0C = 153/01/12 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.1 s ... 30.0 s | [DC Inj Time 2] (tdC) | [Auto DC injection] (AdC-) [Settings] (SEt-) | 440
ADC | Auto DC Injection | 16#28A1 = 10401 | 16#204A/2 | 16#95/01/02 = 149/01/02 | ADC | Configuration and settings | R/W | WORD (Enumeration) | - | [No] (nO) | - | [Auto DC Injection] (AdC) | [CANopen] (CnO-) | 441
SDC1 | Auto DC inj Level 1 | 16#28A3 = 10403 | 16#204A/4 | 16#95/01/04 = 149/01/04 | - | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | (INV * 7 / 10) | Depends of rating | [Auto DC inj Level 1] (SdC1) | [Auto DC injection] (AdC-) [Settings] (SEt-) | 442
TDC1 | Auto DC Inj Time 1 | 16#28A2 = 10402 | 16#204A/3 | 16#95/01/03 = 149/01/03 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.1 s ... 30.0 s | [Auto DC Inj Time 1] (tdC1) | [Auto DC injection] (AdC-) [Settings] (SEt-) | 443
SDC2 | Auto DC inj Level 2 | 16#28A5 = 10405 | 16#204A/6 | 16#95/01/06 = 149/01/06 | - | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | (INV / 2) | Depends of rating | [Auto DC inj Level 2] (SdC2) | [Auto DC injection] (AdC-) [Settings] (SEt-) | 444
TDC2 | Auto DC Inj Time 2 | 16#28A4 = 10404 | 16#204A/5 | 16#95/01/05 = 149/01/05 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.0 s | 0.0 s ... 30.0 s | [Auto DC Inj Time 2] (tdC2) | [Auto DC injection] (AdC-) [Settings] (SEt-) | 445
PS2 | 2 Preset Freq | 16#2C89 = 11401 | 16#2054/2 | 16#9A/01/02 = 154/01/02 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | "NO" | - | [2 Preset Freq] (PS2) | [Preset speeds] (PSS-) | 446
PS4 | 4 Preset Freq | 16#2C8A = 11402 | 16#2054/3 | 16#9A/01/03 = 154/01/03 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | "NO" | - | [4 Preset Freq] (PS4) | [Preset speeds] (PSS-) | 447
PS8 | 8 Preset Freq | 16#2C8B = 11403 | 16#2054/4 | 16#9A/01/04 = 154/01/04 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | "NO" | - | [8 Preset Freq] (PS8) | [Preset speeds] (PSS-) | 448
PS16 | 16 Preset Freq | 16#2C8C = 11404 | 16#2054/5 | 16#9A/01/05 = 154/01/05 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Assigned] (nO) | - | [16 Preset Freq] (PS16) | [Preset speeds] (PSS-) | 449
SP2 | Preset speed 2 | 16#2C92 = 11410 | 16#2054/B | 16#9A/01/0B = 154/01/11 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 10.0 Hz | 0.0 Hz ... 500.0 Hz | [Preset speed 2] (SP2) | [Preset speeds] (PSS-) [Settings] (SEt-) | 450
SP3 | Preset speed 3 | 16#2C93 = 11411 | 16#2054/C | 16#9A/01/0C = 154/01/12 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 15.0 Hz | 0.0 Hz ... 500.0 Hz | [Preset speed 3] (SP3) | [Preset speeds] (PSS-) [Settings] (SEt-) | 451
SP4 | Preset speed 4 | 16#2C94 = 11412 | 16#2054/D | 16#9A/01/0D = 154/01/13 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 20.0 Hz | 0.0 Hz ... 500.0 Hz | [Preset speed 4] (SP4) | [Preset speeds] (PSS-) [Settings] (SEt-) | 452
SP5 | Preset speed 5 | 16#2C95 = 11413 | 16#2054/E | 16#9A/01/0E = 154/01/14 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 25.0 Hz | 0.0 Hz ... 500.0 Hz | [Preset speed 5] (SP5) | [Preset speeds] (PSS-) [Settings] (SEt-) | 453
SP6 | Preset speed 6 | 16#2C96 = 11414 | 16#2054/F | 16#9A/01/0F = 154/01/15 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 30.0 Hz | 0.0 Hz ... 500.0 Hz | [Preset speed 6] (SP6) | [Preset speeds] (PSS-) [Settings] (SEt-) | 454
SP7 | Preset speed 7 | 16#2C97 = 11415 | 16#2054/10 | 16#9A/01/10 = 154/01/16 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 35.0 Hz | 0.0 Hz ... 500.0 Hz | [Preset speed 7] (SP7) | [Preset speeds] (PSS-) [Settings] (SEt-) | 455
SP8 | Preset speed 8 | 16#2C98 = 11416 | 16#2054/11 | 16#9A/01/11 = 154/01/17 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 40.0 Hz | 0.0 Hz ... 500.0 Hz | [Preset speed 8] (SP8) | [Preset speeds] (PSS-) [Settings] (SEt-) | 456
SP9 | Preset speed 9 | 16#2C99 = 11417 | 16#2054/12 | 16#9A/01/12 = 154/01/18 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 45.0 Hz | 0.0 Hz ... 500.0 Hz | [Preset speed 9] (SP9) | [Preset speeds] (PSS-) [Settings] (SEt-) | 457
SP10 | Preset speed 10 | 16#2C9A = 11418 | 16#2054/13 | 16#9A/01/13 = 154/01/19 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 50.0 Hz | 0.0 Hz ... 500.0 Hz | [Preset speed 10] (SP10) | [Preset speeds] (PSS-) [Settings] (SEt-) | 458
SP11 | Preset speed 11 | 16#2C9B = 11419 | 16#2054/14 | 16#9A/01/14 = 154/01/20 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 55.0 Hz | 0.0 Hz ... 500.0 Hz | [Preset speed 11] (SP11) | [Preset speeds] (PSS-) [Settings] (SEt-) | 459
SP12 | Preset speed 12 | 16#2C9C = 11420 | 16#2054/15 | 16#9A/01/15 = 154/01/21 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 60.0 Hz | 0.0 Hz ... 500.0 Hz | [Preset speed 12] (SP12) | [Preset speeds] (PSS-) [Settings] (SEt-) | 460
SP13 | Preset speed 13 | 16#2C9D = 11421 | 16#2054/16 | 16#9A/01/16 = 154/01/22 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 70.0 Hz | 0.0 Hz ... 500.0 Hz | [Preset speed 13] (SP13) | [Preset speeds] (PSS-) [Settings] (SEt-) | 461
SP14 | Preset speed 14 | 16#2C9E = 11422 | 16#2054/17 | 16#9A/01/17 = 154/01/23 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 80.0 Hz | 0.0 Hz ... 500.0 Hz | [Preset speed 14] (SP14) | [Preset speeds] (PSS-) [Settings] (SEt-) | 462
SP15 | Preset speed 15 | 16#2C9F = 11423 | 16#2054/18 | 16#9A/01/18 = 154/01/24 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 90.0 Hz | 0.0 Hz ... 500.0 Hz | [Preset speed 15] (SP15) | [Preset speeds] (PSS-) [Settings] (SEt-) | 463
SP16 | Preset speed 16 | 16#2CA0 = 11424 | 16#2054/19 | 16#9A/01/19 = 154/01/25 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 100.0 Hz | 0.0 Hz ... 500.0 Hz | [Preset speed 16] (SP16) | [Preset speeds] (PSS-) [Settings] (SEt-) | 464
USP | + Speed Assign | 16#2CED = 11501 | 16#2055/2 | 16#9A/01/66 = 154/01/102 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Assigned] (nO) | - | [+ Speed Assign] (USP) | [+/- speed] (UPd-) | 465
DSP | - Speed Assign | 16#2CEE = 11502 | 16#2055/3 | 16#9A/01/67 = 154/01/103 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Assigned] (nO) | - | [- Speed Assign] (dSP) | [+/- speed] (UPd-) | 466
STR | Ref Frequency Save | 16#2CEF = 11503 | 16#2055/4 | 16#9A/01/68 = 154/01/104 | STR | Configuration and settings | R/WS | WORD (Enumeration) | - | [No Save] (nO) | - | [Ref Frequency Save] (Str) | [Motor monitoring] (MOP-) | 467
AST | Angle setting type | 16#3665 = 13925 | 16#206D/1A | 16#A6/01/7E = 166/01/126 | AST | Configuration and settings | R/WS | WORD (Enumeration) | - | [PSIO align.] (PSIO) | - | [Angle setting type] (ASt) | [data] (Mtd-) [Motor tune] (MtU-) | 468
MCR | PSI Align Curr Max | 16#3CF7 = 15607 | 16#207E/8 | 16#AF/01/08 = 175/01/08 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | [Auto] (AUtO) | [Auto] (AUtO) ... 300 % | [PSI Align Curr Max] (MCr) | [data] (Mtd-) [Motor tune] (MtU-) | 469
PIF | PID feedback | 16#2E7D = 11901 | 16#2059/2 | 16#9C/01/66 = 156/01/102 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | "NO" | - | [PID feedback] (PIF) | [Feedback] (Fdb-) | 470
PIF1 | Min PID feedback | 16#2E80 = 11904 | 16#2059/5 | 16#9C/01/69 = 156/01/105 | - | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | Refer to programming manual | [Min PID feedback] (PIF1) | [Feedback] (Fdb-) | 471
PIF2 | Max PID feedback | 16#2E81 = 11905 | 16#2059/6 | 16#9C/01/6A = 156/01/106 | - | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | Refer to programming manual | [Max PID feedback] (PIF2) | [Feedback] (Fdb-) | 472
PIP1 | Min PID Process | 16#2E82 = 11906 | 16#2059/7 | 16#9C/01/6B = 156/01/107 | - | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | Refer to programming manual | [Min PID Process] (PIP1) | [Reference frequency] (rF-) | 473
PIP2 | Max PID Process | 16#2E83 = 11907 | 16#2059/8 | 16#9C/01/6C = 156/01/108 | - | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | Refer to programming manual | [Max PID Process] (PIP2) | [Reference frequency] (rF-) | 474
PII | Intern PID Ref | 16#2E84 = 11908 | 16#2059/9 | 16#9C/01/6D = 156/01/109 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Intern PID Ref] (PII) | [Reference frequency] (rF-) | 475
RPI | Internal PID ref | 16#2E90 = 11920 | 16#2059/15 | 16#9C/01/79 = 156/01/121 | - | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | Refer to programming manual | [Internal PID ref] (rPI) | [PID display] (PIC-) [Display] (SUP-) | 476
RPG | PID Prop.Gain | 16#2EA5 = 11941 | 16#2059/2A | 16#9C/01/8E = 156/01/142 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 | 1.00 | 0.01 ... 100.00 | [PID Prop.Gain] (rPG) | [Settings] (SEt-) [Settings] (St-) | 477
RIG | PID Intgl.Gain | 16#2EA6 = 11942 | 16#2059/2B | 16#9C/01/8F = 156/01/143 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 | 1.00 | 0.01 ... 100.00 | [PID Intgl.Gain] (rIG) | [Settings] (SEt-) [Settings] (St-) | 478
RDG | PID derivative gain | 16#2EA7 = 11943 | 16#2059/2C | 16#9C/01/90 = 156/01/144 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 | 0.00 | 0.00 ... 100.00 | [PID derivative gain] (rdG) | [Settings] (SEt-) [Settings] (St-) | 479
PRP | PID ramp | 16#2ED0 = 11984 | 16#2059/55 | 16#9C/01/B9 = 156/01/185 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.0 s | 0.0 s ... 99.9 s | [PID ramp] (PrP) | [Settings] (SEt-) [Settings] (St-) | 480
PIC | PID Inversion | 16#2EA4 = 11940 | 16#2059/29 | 16#9C/01/8D = 156/01/141 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [PID Inversion] (PIC) | [Settings] (St-) | 481
POL | PID Min Output | 16#2EB0 = 11952 | 16#2059/35 | 16#9C/01/99 = 156/01/153 | - | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | 0.0 Hz | -500.0 Hz ... 500.0 Hz | [PID Min Output] (POL) | [Settings] (SEt-) [Settings] (St-) | 482
POH | PID Max Output | 16#2EB1 = 11953 | 16#2059/36 | 16#9C/01/9A = 156/01/154 | - | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | 60.0 Hz | 0.0 Hz ... 500.0 Hz | [PID Max Output] (POH) | [Settings] (SEt-) [Settings] (St-) | 483
PAL | Min fbk Warning | 16#2EB9 = 11961 | 16#2059/3E | 16#9C/01/A2 = 156/01/162 | - | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | 0 ... 65535 | [Min fbk Warning] (PAL) | [Settings] (SEt-) [Feedback] (Fdb-) | 484
PAH | Max fbk Warning | 16#2EBA = 11962 | 16#2059/3F | 16#9C/01/A3 = 156/01/163 | - | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | 0 ... 65535 | [Max fbk Warning] (PAH) | [Settings] (SEt-) [Feedback] (Fdb-) | 485
PER | PID error Warning | 16#2EBB = 11963 | 16#2059/40 | 16#9C/01/A4 = 156/01/164 | - | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | 0 ... 65535 | [PID error Warning] (PEr) | [Settings] (SEt-) [Settings] (St-) | 486
PIS | PID Integral OFF | 16#2EA8 = 11944 | 16#2059/2D | 16#9C/01/91 = 156/01/145 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | "NO" | - | [PID Integral OFF] (PIS) | [Settings] (St-) | 487
FPI | Predictive Speed Ref | 16#2EAE = 11950 | 16#2059/33 | 16#9C/01/97 = 156/01/151 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Configured] (nO) | - | [Predictive Speed Ref] (FPI) | [Reference frequency] (rF-) | 488
PSR | Speed input % | 16#2EAF = 11951 | 16#2059/34 | 16#9C/01/98 = 156/01/152 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 100 % | 1 % ... 100 % | [Speed input %] (PSr) | [Pre-settings] (PrES-) | 489
PAU | Auto/Manual assign. | 16#2EC2 = 11970 | 16#2059/47 | 16#9C/01/AB = 156/01/171 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Assigned] (nO) | - | [Auto/Manual assign.] (PAU) | [Reference frequency] (rF-) | 490
PIM | Manual PID reference | 16#2EB2 = 11954 | 16#2059/37 | 16#9C/01/9B = 156/01/155 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Configured] (nO) | - | [Manual PID reference] (PIM) | [Reference frequency] (rF-) | 491
TLS | Low Speed Timeout | 16#2DB5 = 11701 | 16#2057/2 | 16#9B/01/66 = 155/01/102 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.0 s | 0.0 s ... 999.9 s | [Low Speed Timeout] (tLS) | [Stop after speed timeout] (PrSP-) [Settings] (SEt-) | 492
PR2 | 2 PID Preset Assign | 16#2E85 = 11909 | 16#2059/A | 16#9C/01/6E = 156/01/110 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | "NO" | - | [2 PID Preset Assign] (Pr2) | [PID preset references] (PrI-) | 493
PR4 | 4 PID Preset Assign | 16#2E86 = 11910 | 16#2059/B | 16#9C/01/6F = 156/01/111 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | "NO" | - | [4 PID Preset Assign] (Pr4) | [PID preset references] (PrI-) | 494
RP2 | Ref PID Preset 2 | 16#2E91 = 11921 | 16#2059/16 | 16#9C/01/7A = 156/01/122 | - | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | Refer to programming manual | [Ref PID Preset 2] (rP2) | [Settings] (SEt-) | 495
RP3 | Ref PID Preset 3 | 16#2E92 = 11922 | 16#2059/17 | 16#9C/01/7B = 156/01/123 | - | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | Refer to programming manual | [Ref PID Preset 3] (rP3) | [PDO3 image] (P03-) | 496
RP4 | Ref PID Preset 4 | 16#2E93 = 11923 | 16#2059/18 | 16#9C/01/7C = 156/01/124 | - | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | Refer to programming manual | [Ref PID Preset 4] (rP4) | [Settings] (SEt-) [PID preset references] (PrI-) | 497
TLA | Torque limit activ. | 16#23FA = 9210 | 16#203E/B | 16#8F/01/0B = 143/01/11 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | "NO" | - | [Torque limit activ.] (tLA) | [Torque limitation] (tOL-) | 498
LLC | Mains Contactor | 16#3522 = 13602 | 16#206A/3 | 16#A5/01/03 = 165/01/03 | CSLOUT | Configuration and settings | R/WS | WORD (Enumeration) | - |  | - | [Mains Contactor] (LLC) | [Mains contactor command] (LLC-) | 499
LES | Drive Lock | 16#3521 = 13601 | 16#206A/2 | 16#A5/01/02 = 165/01/02 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Assigned] (nO) | - | [Drive Lock] (LES) | [Mains contactor command] (LLC-) | 500
LCT | Mains V. time out | 16#3523 = 13603 | 16#206A/4 | 16#A5/01/04 = 165/01/04 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 s | 5 s | 1 s ... 999 s | [Mains V. time out] (LCt) | [Mains contactor command] (LLC-) [Circuit breaker] (CCb -) | 501
TUL | Autotuning Assign | 16#258A = 9610 | 16#2042/B | 16#91/01/0B = 145/01/11 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Assigned] (nO) | - | [Autotuning Assign] (tUL) | [Motor tune] (MtU-) | 502
RSF | Fault Reset Assign | 16#1BD4 = 7124 | 16#2029/19 | 16#84/01/7D = 132/01/125 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | "LI4" | - | [Fault Reset Assign] (rSF) | [Fault reset] (rSt-) | 503
RP | Product restart | 16#1BD8 = 7128 | 16#2029/1D | 16#84/01/81 = 132/01/129 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Product restart] (rP) | [Fault reset] (rSt-) | 504
RPA | Prod Restart Assign | 16#1BD9 = 7129 | 16#2029/1E | 16#84/01/82 = 132/01/130 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Assigned] (nO) | - | [Prod Restart Assign] (rPA) | [Fault reset] (rSt-) | 505
ATR | Auto Fault Reset | 16#1BD2 = 7122 | 16#2029/17 | 16#84/01/7B = 132/01/123 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Auto Fault Reset] (Atr) | [Fan] (CSFA-) [Auto Fault Reset] (Atr-) | 506
TAR | Fault Reset Time | 16#1BD3 = 7123 | 16#2029/18 | 16#84/01/7C = 132/01/124 | DUR | Configuration and settings | R/WS | WORD (Enumeration) | - | [5 minutes] (5) | - | [Fault Reset Time] (tAr) | [Auto Fault Reset] (Atr-) | 507
FLR | Catch On Fly | 16#0C26 = 3110 | 16#2001/B | 16#70/01/6F = 112/01/111 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Catch On Fly] (FLr) | [Fan] (CSFA-) [Catch on the fly] (FLr-) | 508
THT | Motor Thermal Mode | 16#258C = 9612 | 16#2042/D | 16#91/01/0D = 145/01/13 | THT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Self cooled] (ACL) | - | [Motor Thermal Mode] (tHt) | [Motor thermal monit] (tHt-) [Motor monitoring] (MOP-) | 509
TTD | Motor Therm Thd | 16#2AFA = 11002 | 16#2050/3 | 16#98/01/03 = 152/01/03 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 100 % | 0 % ... 118 % | [Motor Therm Thd] (ttd) | [Threshold reached] (tHrE-) [Motor monitoring] (MOP-) [Settings] (SEt-) | 510
OLL | MotorTemp ErrorResp | 16#1B61 = 7009 | 16#2028/A | 16#84/01/0A = 132/01/10 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel Stop] (YES) | - | [MotorTemp ErrorResp] (OLL) | [Motor monitoring] (MOP-) | 511
OPL | OutPhaseLoss Assign | 16#258B = 9611 | 16#2042/C | 16#91/01/0C = 145/01/12 | OPL | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual | - | [OutPhaseLoss Assign] (OPL) | [Output phase loss] (OPL-) | 512
ODT | OutPhaseLoss Delay | 16#1BA9 = 7081 | 16#2028/52 | 16#84/01/52 = 132/01/82 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.5 s ... 10.0 s | [OutPhaseLoss Delay] (Odt) | [Output phase loss] (OPL-) | 513
IPL | InPhaseLoss Assign | 16#1B5A = 7002 | 16#2028/3 | 16#84/01/03 = 132/01/03 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | @EP@ | - | [InPhaseLoss Assign] (IPL) | [Input phase loss] (IPL-) | 514
OHL | DriveTemp ErrorResp | 16#1B60 = 7008 | 16#2028/9 | 16#84/01/09 = 132/01/09 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel Stop] (YES) | - | [DriveTemp ErrorResp] (OHL) | [Drive overload monit] (Obr-) | 515
THA | Drv Thermal Warning | 16#2B01 = 11009 | 16#2050/A | 16#98/01/0A = 152/01/10 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 100 % | 0 % ... 118 % | [Drv Thermal Warning] (tHA) | [Drive overload monit] (Obr-) | 516
ETF | Ext Error assign | 16#1BDB = 7131 | 16#2029/20 | 16#84/01/84 = 132/01/132 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | "NO" | - | [Ext Error assign] (EtF) | [External error] (EtF-) | 517
EPL | Ext Error Resp | 16#1B5E = 7006 | 16#2028/7 | 16#84/01/07 = 132/01/07 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel Stop] (YES) | - | [Ext Error Resp] (EPL) | [External error] (EtF-) | 518
USB | Undervoltage Resp | 16#35EB = 13803 | 16#206C/4 | 16#A6/01/04 = 166/01/04 | USB | Configuration and settings | R/WS | WORD (Enumeration) | - | [Error Triggered] (0) | - | [Undervoltage Resp] (USb) | [Undervoltage handling] (USb-) | 519
URES | Mains voltage | 16#35E9 = 13801 | 16#206C/2 | 16#A6/01/02 = 166/01/02 | URES | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual | - | [Mains voltage] (UrES) | [Undervoltage handling] (USb-) | 520
USL | Undervoltage level | 16#35EA = 13802 | 16#206C/3 | 16#A6/01/03 = 166/01/03 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | (call USL_Max []) | 100 V ... 345 V | [Undervoltage level] (USL) | [Undervoltage handling] (USb-) | 521
UST | UnderVolt timeout | 16#35EC = 13804 | 16#206C/5 | 16#A6/01/05 = 166/01/05 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 s | 0.2 s | 0.2 s ... 999.9 s | [UnderVolt timeout] (USt) | [Undervoltage handling] (USb-) | 522
STP | Stop Type PLoss | 16#1B5C = 7004 | 16#2028/5 | 16#84/01/05 = 132/01/05 | STP | Configuration and settings | R/WS | WORD (Enumeration) | - | [Inactive] (nO) | - | [Stop Type PLoss] (StP) | [Undervoltage handling] (USb-) | 523
TSM | UnderV. restart tm | 16#35F5 = 13813 | 16#206C/E | 16#A6/01/0E = 166/01/14 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 1.0 s | 1.0 s ... 999.9 s | [UnderV. restart tm] (tSM) | [Undervoltage handling] (USb-) | 524
UPL | Prevention level | 16#35F3 = 13811 | 16#206C/C | 16#A6/01/0C = 166/01/12 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | (call USH_Max []) | 141 V ... 414 V | [Prevention level] (UPL) | [Undervoltage handling] (USb-) | 525
STM | Max stop time | 16#35F6 = 13814 | 16#206C/F | 16#A6/01/0F = 166/01/15 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 1.00 s | 0.01 s ... 60.00 s | [Max stop time] (StM) | [Undervoltage handling] (USb-) | 526
TBS | DC bus maintain time | 16#35F4 = 13812 | 16#206C/D | 16#A6/01/0D = 166/01/13 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | 9999 s | 1 s ... 9999 s | [DC bus maintain time] (tbS) | [Undervoltage handling] (USb-) | 527
STRT | Output Short Circuit Test | 16#0C28 = 3112 | 16#2001/D | 16#70/01/71 = 112/01/113 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [Yes] (YES) | - | [Output Short Circuit Test] (Strt) | [Motor monitoring] (MOP-) | 528
LFL3 | AI3 4-20mA loss | 16#1B65 = 7013 | 16#2028/E | 16#84/01/0E = 132/01/14 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ignore] (nO) | - | [AI3 4-20mA loss] (LFL3) | [4-20 mA loss] (LFL-) | 529
INH | ErrorDetect Disable | 16#1BD5 = 7125 | 16#2029/1A | 16#84/01/7E = 132/01/126 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Assigned] (nO) | - | [ErrorDetect Disable] (InH) | [Fan] (CSFA-) [Error detection disable] (InH-) | 530
CLL | Fieldbus Interrupt Resp | 16#1B67 = 7015 | 16#2028/10 | 16#84/01/10 = 132/01/16 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel Stop] (YES) | - | [Fieldbus Interrupt Resp] (CLL) | [Communication Module] (COMO-) | 531
COL | CANopen Error Resp | 16#1B63 = 7011 | 16#2028/C | 16#84/01/0C = 132/01/12 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel Stop] (YES) | - | [CANopen Error Resp] (COL) | [Communication Module] (COMO-) | 532
SLL | Modbus Error Resp | 16#1B62 = 7010 | 16#2028/B | 16#84/01/0B = 132/01/11 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel Stop] (YES) | - | [Modbus Error Resp] (SLL) | [Fieldbus monitoring] (CLL-) | 533
TNL | Tuning Error Resp | 16#1B64 = 7012 | 16#2028/D | 16#84/01/0D = 132/01/13 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel Stop] (YES) | - | [Tuning Error Resp] (tnL) | [Motor tune] (MtU-) | 534
PPI | Pairing password | 16#36B1 = 14001 | 16#206E/2 | 16#A7/01/02 = 167/01/02 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | [OFF] (OFF) | [OFF] (OFF) ... 9999 | [Pairing password] (PPI) | [My preferences] (MYP-) | 535
LFF | FallbackSpeed | 16#1BA8 = 7080 | 16#2028/51 | 16#84/01/51 = 132/01/81 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 500.0 Hz | [FallbackSpeed] (LFF) | [4-20 mA loss] (LFL-) | 536
NCA1 | Scan.Out1 address | 16#31B1 = 12721 | 16#2061/16 | 16#A0/01/7A = 160/01/122 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 8501 | 0 ... 65535 |  |  | 537
NCA2 | Scan.Out2 address | 16#31B2 = 12722 | 16#2061/17 | 16#A0/01/7B = 160/01/123 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 8602 | 0 ... 65535 |  |  | 538
NCA3 | Scan.Out3 address | 16#31B3 = 12723 | 16#2061/18 | 16#A0/01/7C = 160/01/124 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 539
NCA4 | Scan.Out4 address | 16#31B4 = 12724 | 16#2061/19 | 16#A0/01/7D = 160/01/125 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 540
NCA5 | Scan.Out5 address | 16#31B5 = 12725 | 16#2061/1A | 16#A0/01/7E = 160/01/126 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 541
NCA6 | Scan.Out6 address | 16#31B6 = 12726 | 16#2061/1B | 16#A0/01/7F = 160/01/127 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 542
NCA7 | Scan.Out7 address | 16#31B7 = 12727 | 16#2061/1C | 16#A0/01/80 = 160/01/128 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 543
NCA8 | Scan.Out8 address | 16#31B8 = 12728 | 16#2061/1D | 16#A0/01/81 = 160/01/129 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 544
NMA1 | Scan. IN1 address | 16#319D = 12701 | 16#2061/2 | 16#A0/01/66 = 160/01/102 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 3201 | 0 ... 65535 |  |  | 545
NMA2 | Scan. IN2 address | 16#319E = 12702 | 16#2061/3 | 16#A0/01/67 = 160/01/103 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 8604 | 0 ... 65535 |  |  | 546
NMA3 | Scan. IN3 address | 16#319F = 12703 | 16#2061/4 | 16#A0/01/68 = 160/01/104 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 547
NMA4 | Scan. IN4 address | 16#31A0 = 12704 | 16#2061/5 | 16#A0/01/69 = 160/01/105 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 548
NMA5 | Scan. IN5 address | 16#31A1 = 12705 | 16#2061/6 | 16#A0/01/6A = 160/01/106 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 549
NMA6 | Scan. IN6 address | 16#31A2 = 12706 | 16#2061/7 | 16#A0/01/6B = 160/01/107 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 550
NMA7 | Scan. IN7 address | 16#31A3 = 12707 | 16#2061/8 | 16#A0/01/6C = 160/01/108 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 551
NMA8 | Scan. IN8 address | 16#31A4 = 12708 | 16#2061/9 | 16#A0/01/6D = 160/01/109 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 552
OMA1 | Scan. IN1 address | 16#3C29 = 15401 | 16#207C/2 | 16#AE/01/02 = 174/01/02 | - | Configuration and settings | [always] | UINT (Unsigned16) | 1 | 3201 | 0 ... 65535 |  |  | 553
OMA2 | Scan. IN2 address | 16#3C2A = 15402 | 16#207C/3 | 16#AE/01/03 = 174/01/03 | - | Configuration and settings | [always] | UINT (Unsigned16) | 1 | 8604 | 0 ... 65535 |  |  | 554
OMA3 | Scan. IN3 address | 16#3C2B = 15403 | 16#207C/4 | 16#AE/01/04 = 174/01/04 | - | Configuration and settings | [always] | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 555
OMA4 | Scan. IN4 address | 16#3C2C = 15404 | 16#207C/5 | 16#AE/01/05 = 174/01/05 | - | Configuration and settings | [always] | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 556
OMA5 | Scan. IN5 address | 16#3C2D = 15405 | 16#207C/6 | 16#AE/01/06 = 174/01/06 | - | Configuration and settings | [always] | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 557
OMA6 | Scan. IN6 address | 16#3C2E = 15406 | 16#207C/7 | 16#AE/01/07 = 174/01/07 | - | Configuration and settings | [always] | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 558
OCA1 | Scan.Out1 address | 16#3C3D = 15421 | 16#207C/16 | 16#AE/01/16 = 174/01/22 | - | Configuration and settings | [always] | UINT (Unsigned16) | 1 | 8501 | 0 ... 65535 |  |  | 559
OCA2 | Scan.Out2 address | 16#3C3E = 15422 | 16#207C/17 | 16#AE/01/17 = 174/01/23 | - | Configuration and settings | [always] | UINT (Unsigned16) | 1 | 8602 | 0 ... 65535 |  |  | 560
OCA3 | Scan.Out3 address | 16#3C3F = 15423 | 16#207C/18 | 16#AE/01/18 = 174/01/24 | - | Configuration and settings | [always] | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 561
OCA4 | Scan.Out4 address | 16#3C40 = 15424 | 16#207C/19 | 16#AE/01/19 = 174/01/25 | - | Configuration and settings | [always] | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 562
OCA5 | Scan.Out5 address | 16#3C41 = 15425 | 16#207C/1A | 16#AE/01/1A = 174/01/26 | - | Configuration and settings | [always] | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 563
OCA6 | Scan.Out6 address | 16#3C42 = 15426 | 16#207C/1B | 16#AE/01/1B = 174/01/27 | - | Configuration and settings | [always] | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 564
ADD | Modbus Address | 16#1771 = 6001 | 16#201E/2 | 16#7F/01/02 = 127/01/02 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | [OFF] (OFF) | [OFF] (OFF) ... 247 | [Modbus Address] (Add) | [Modbus Fieldbus] (Md1-) | 565
AMOC | Modbus add Com.C. | 16#19FB = 6651 | 16#2024/34 | 16#82/01/34 = 130/01/52 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | [OFF] (OFF) | [OFF] (OFF) ... 247 | [Modbus add Com.C.] (AMOC) | [Modbus Fieldbus] (Md1-) | 566
TBR | Modbus baud rate | 16#1773 = 6003 | 16#201E/4 | 16#7F/01/04 = 127/01/04 | TBR | Configuration and settings | R/WS | WORD (Enumeration) | - | [19200 bps] (19 2) | - | [Modbus baud rate] (tbr) | [Modbus Fieldbus] (Md1-) | 567
TFO | Modbus Format | 16#1774 = 6004 | 16#201E/5 | 16#7F/01/05 = 127/01/05 | FOR | Configuration and settings | R/WS | WORD (Enumeration) | - | [8-E-1] (8E1) | - | [Modbus Format] (tFO) | [Modbus Fieldbus] (Md1-) | 568
TTO | ModbusTimeout | 16#1775 = 6005 | 16#201E/6 | 16#7F/01/06 = 127/01/06 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 s | 10.0 s | 0.1 s ... 30.0 s | [ModbusTimeout] (ttO) | [Modbus Fieldbus] (Md1-) | 569
ADCO | CANopen Address | 16#17A3 = 6051 | 16#201E/34 | 16#7F/01/34 = 127/01/52 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | [OFF] (OFF) | [OFF] (OFF) ... 127 | [CANopen Address] (AdCO) | [CANopen] (CnO-) | 570
BDCO | CANopen Baudrate | 16#17A5 = 6053 | 16#201E/36 | 16#7F/01/36 = 127/01/54 | BDCO | Configuration and settings | R/WS | WORD (Enumeration) | - | [250 kbps] (250 ) | - | [CANopen Baudrate] (bdCO) | [CANopen] (CnO-) | 571
ERCO | CANopen Error | 16#17A8 = 6056 | 16#201E/39 | 16#7F/01/39 = 127/01/57 | - | Configuration and settings | R | UINT (Unsigned16) | 1 |  | 0 ... 5 | [CANopen Error] (ErCO) | [CANopen map] (CnM-) [CANopen] (CnO-) | 572
FLO | Forced Local Assign | 16#20EF = 8431 | 16#2036/20 | 16#8B/01/20 = 139/01/32 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Assigned] (nO) | - | [Forced Local Assign] (FLO) | [Command and Reference] (CrP-) | 573
FLOC | Forced Local Freq | 16#20F0 = 8432 | 16#2036/21 | 16#8B/01/21 = 139/01/33 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Configured] (nO) | - | [Forced Local Freq] (FLOC) | [Command and Reference] (CrP-) | 574
FLOT | Time-out forc. local | 16#20F1 = 8433 | 16#2036/22 | 16#8B/01/22 = 139/01/34 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 s | 10.0 s | 0.1 s ... 30.0 s | [Time-out forc. local] (FLOt) | [Command and Reference] (CrP-) | 575
ADRC | Address | 16#19C9 = 6601 | 16#2024/2 | 16#82/01/02 = 130/01/02 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | Refer to programming manual | 0 ... 65535 | [Address] (AdrC) | [DeviceNet] (dnC-) [Profibus] (PbC-) | 576
PRFL | PPO profile used | 16#1A09 = 6665 | 16#2024/42 | 16#82/01/42 = 130/01/66 | PRFL | Configuration and settings | [always] | WORD (Enumeration) | - | Refer to programming manual | - | [PPO profile used] (PrFL) | [PROFIBUS DIAG] (Prb-) [PROFINET DIAG] (Prn-) | 577
DPMA | DP Master Active | 16#1A0A = 6666 | 16#2024/43 | 16#82/01/43 = 130/01/67 | DPMA | Communication parameters | [always] | WORD (Enumeration) | - | [MCL1] (1) | - | [DP Master Active] (dPMA) | [PROFIBUS DIAG] (Prb-) [PROFINET DIAG] (Prn-) | 578
CIOA | Conf. Assembly | 16#1A0B = 6667 | 16#2024/44 | 16#82/01/44 = 130/01/68 | CIOA | Configuration and settings | [always] | WORD (Enumeration) | - | [21/71] (21) | - | [Conf. Assembly] (CIOA) | [DeviceNet] (dnC-) | 579
BDR | Bit rate | 16#19CB = 6603 | 16#2024/4 | 16#82/01/04 = 130/01/04 | TBR | Configuration and settings | R/WS | WORD (Enumeration) | - | [Automatic] (AUtO) | - | [Bit rate] (bdr) | [DeviceNet] (dnC-) | 580
BDRU | Data rate used | 16#1A04 = 6660 | 16#2024/3D | 16#82/01/3D = 130/01/61 | TBR | Configuration and settings | [always] | WORD (Enumeration) | - | [Automatic] (AUtO) | - | [Data rate used] (bdrU) | [DEVICENET DIAG] (dUn-) [PROFIBUS DIAG] (Prb-) | 581
RDS |  | 16#FAFB = 64251 |  | = | RDS | Configuration and settings | R/W | WORD (Enumeration) | - | [Auto] (AUtO) | - |  |  | 582
EWE | Services | 16#FB08 = 64264 |  | = | EWE | Configuration and settings | R/W | WORD (BitString16) | - | 0 | - |  |  | 583
ARD | Actual rate | 16#FB0A = 64266 |  | = | RDS | Configuration and settings | R | WORD (Enumeration) | - |  | - | [Actual rate] (Ard) | [Ethernet Emb Diag] (MPE-) | 584
L1D | DI1 Delay | 16#0FA1 = 4001 | 16#200A/2 | 16#75/01/02 = 117/01/02 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 5 ms | 0 ms ... 200 ms | [DI1 Delay] (L1d) | [DI1 Configuration] (dI1-) | 585
R1 | R1 Assignment | 16#1389 = 5001 | 16#2014/2 | 16#7A/01/02 = 122/01/02 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Operating State Fault] (FLt) | - | [R1 Assignment] (r1) | [R1 configuration] (r1-) | 586
R2 | R2 Assignment | 16#138A = 5002 | 16#2014/3 | 16#7A/01/03 = 122/01/03 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | "NO" | - | [R2 Assignment] (r2) | [R2 configuration] (r2-) | 587
L2D | DI2 Delay | 16#0FA2 = 4002 | 16#200A/3 | 16#75/01/03 = 117/01/03 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 5 ms | 0 ms ... 200 ms | [DI2 Delay] (L2d) | [DI2 Configuration] (dI2-) | 588
R1D | R1 Delay time | 16#1091 = 4241 | 16#200C/2A | 16#76/01/2A = 118/01/42 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [R1 Delay time] (r1d) | [R1 configuration] (r1-) | 589
R2D | R2 Delay time | 16#1092 = 4242 | 16#200C/2B | 16#76/01/2B = 118/01/43 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [R2 Delay time] (r2d) | [R2 configuration] (r2-) | 590
L3D | DI3 Delay | 16#0FA3 = 4003 | 16#200A/4 | 16#75/01/04 = 117/01/04 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 5 ms | 0 ms ... 200 ms | [DI3 Delay] (L3d) | [DI3 Configuration] (dI3-) | 591
R1S | R1 Active at | 16#1069 = 4201 | 16#200C/2 | 16#76/01/02 = 118/01/02 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [1] (POS) | - | [R1 Active at] (r1S) | [R1 configuration] (r1-) | 592
R2S | R2 Active at | 16#106A = 4202 | 16#200C/3 | 16#76/01/03 = 118/01/03 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [1] (POS) | - | [R2 Active at] (r2S) | [R2 configuration] (r2-) | 593
L4D | DI4 Delay | 16#0FA4 = 4004 | 16#200A/5 | 16#75/01/05 = 117/01/05 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 5 ms | 0 ms ... 200 ms | [DI4 Delay] (L4d) | [DI4 Configuration] (dI4-) | 594
R1H | R1 Holding time | 16#107D = 4221 | 16#200C/16 | 16#76/01/16 = 118/01/22 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [R1 Holding time] (r1H) | [R1 configuration] (r1-) | 595
R2H | R2 Holding time | 16#107E = 4222 | 16#200C/17 | 16#76/01/17 = 118/01/23 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [R2 Holding time] (r2H) | [R2 configuration] (r2-) | 596
L5D | DI5 Delay | 16#0FA5 = 4005 | 16#200A/6 | 16#75/01/06 = 117/01/06 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 5 ms | 0 ms ... 200 ms | [DI5 Delay] (L5d) | [DI5 Configuration] (dI5-) | 597
L6D | DI6 Delay | 16#0FA6 = 4006 | 16#200A/7 | 16#75/01/07 = 117/01/07 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 5 ms | 0 ms ... 200 ms | [DI6 Delay] (L6d) | [DI6 Configuration] (dI6-) | 598
FRHT | FRH high resolution | 16#0C96 = 3222 | 16#2002/17 | 16#71/01/17 = 113/01/23 | - | Configuration and settings | R | INT (Signed16) | 1 |  | -32767 ... 32767 |  |  | 599
SLCR | LCR without filter | 16#0C98 = 3224 | 16#2002/19 | 16#71/01/19 = 113/01/25 | - | Configuration and settings | R | UINT (Unsigned16) | Refer to programming manual |  | Depends of rating |  |  | 600
SRFR | RFR without filter | 16#0C99 = 3225 | 16#2002/1A | 16#71/01/1A = 113/01/26 | - | Configuration and settings | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz |  |  | 601
SOTR | OTR without filter | 16#0C9A = 3226 | 16#2002/1B | 16#71/01/1B = 113/01/27 | - | Configuration and settings | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % |  |  | 602
SULN | ULN without filter | 16#0C9D = 3229 | 16#2002/1E | 16#71/01/1E = 113/01/30 | - | Configuration and settings | R | UINT (Unsigned16) | 0.1 V |  | [No meas.] (----) ... 6553.5 V |  |  | 603
SOPR | OPR without filter | 16#0CDA = 3290 | 16#2002/5B | 16#71/01/5B = 113/01/91 | - | Configuration and settings | R | INT (Signed16) | 1 % |  | -32767 % ... 32767 % |  |  | 604
SAI1 | AI1 physical value without filter | 16#14AB = 5291 | 16#2016/5C | 16#7B/01/5C = 123/01/92 | - | Measurement parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 |  |  | 605
SAI2 | AI2 physical value without filter | 16#14AC = 5292 | 16#2016/5D | 16#7B/01/5D = 123/01/93 | - | Measurement parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 |  |  | 606
SAI3 | AI3 physical value without filter | 16#14AD = 5293 | 16#2016/5E | 16#7B/01/5E = 123/01/94 | - | Measurement parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 |  |  | 607
SAO1 | AO1 physical value without filter | 16#14AF = 5295 | 16#2016/60 | 16#7B/01/60 = 123/01/96 | - | Actual values parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 |  |  | 608
ULT | Unld T. Del. Detect | 16#384B = 14411 | 16#2072/C | 16#A9/01/0C = 169/01/12 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 s | 0 s | 0 s ... 100 s | [Unld T. Del. Detect] (ULt) | [Process underload] (ULd-) | 609
SRB | Hysteresis Freq | 16#3841 = 14401 | 16#2072/2 | 16#A9/01/02 = 169/01/02 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.3 Hz | 0.3 Hz ... 500.0 Hz | [Hysteresis Freq] (Srb) | [Process underload] (ULd-) [Process overload] (OLd-) [Settings] (SEt-) | 610
UDL | Underload Mangmt. | 16#384C = 14412 | 16#2072/D | 16#A9/01/0D = 169/01/13 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel Stop] (YES) | - | [Underload Mangmt.] (UdL) | [Process underload] (ULd-) | 611
RMUD | Unld. FreqThr. Det. | 16#384E = 14414 | 16#2072/F | 16#A9/01/0F = 169/01/15 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 500.0 Hz | [Unld. FreqThr. Det.] (rMUd) | [Process underload] (ULd-) [Settings] (SEt-) | 612
LUL | Unld.Thr.0.Speed | 16#384F = 14415 | 16#2072/10 | 16#A9/01/10 = 169/01/16 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [Unld.Thr.0.Speed] (LUL) | [Process underload] (ULd-) [Settings] (SEt-) | 613
LUN | Unld.Thr.Nom.Speed | 16#3850 = 14416 | 16#2072/11 | 16#A9/01/11 = 169/01/17 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 60 % | 20 % ... 100 % | [Unld.Thr.Nom.Speed] (LUn) | [Process underload] (ULd-) [Settings] (SEt-) | 614
TOL | Ovld Time Detect. | 16#3855 = 14421 | 16#2072/16 | 16#A9/01/16 = 169/01/22 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 s | 0 s | 0 s ... 100 s | [Ovld Time Detect.] (tOL) | [Process overload] (OLd-) | 615
ODL | Ovld.Proces.Mngmt | 16#3856 = 14422 | 16#2072/17 | 16#A9/01/17 = 169/01/23 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel Stop] (YES) | - | [Ovld.Proces.Mngmt] (OdL) | [Process overload] (OLd-) | 616
STOS | STO fct status | 16#3BDA = 15322 | 16#207B/17 | 16#AD/01/7B = 173/01/123 | STOS | Safety function | R | WORD (Enumeration) | - |  | - |  |  | 617
ACCP | PID acceleration time | 16#2ED1 = 11985 | 16#2059/56 | 16#9C/01/BA = 156/01/186 | - | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | Refer to programming manual | [PID acceleration time] (ACCP) | [Settings] (SEt-) [Settings] (St-) | 618
ACCS | Start Accel Ramp | 16#2350 = 9040 | 16#203C/29 | 16#8E/01/29 = 142/01/41 | - | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | [No] (nO) | Refer to programming manual | [Start Accel Ramp] (ACCS) | [Settings] (SEt-) [Pump start stop] (PSt-) | 619
AI1I |  | 16#1466 = 5222 | 16#2016/17 | 16#7B/01/17 = 123/01/23 | - | Measurement parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767 |  |  | 620
AI1J | AI1 Lowest Process | 16#1196 = 4502 | 16#200F/3 | 16#77/01/67 = 119/01/103 | - | Configuration and settings | R/WS | INT (Signed16) | 1 | 0 | -32767 ... 32767 | [AI1 Lowest Process] (AI1J) | [AI1 sensor config.] (ICA1-) [AI1 Sensor Config.] (OCA1-) [AI1 sensor config.] (IF1-) [AI1 sensor config.] (HIF1-) [AI1 Installation Flow] (FIF1-) [AI1 Sensor Config.] (LF1-) [AI1 Sensor Config.] (bIF1-) [AI1 Configuration] (LIF1-) [AI1 Sensor config.] (PF1-) [AI1 Sensor config.] (nPF1-) [AI1 sensor config.] (IPA1-) [AI1 Configuration] (PPA1-) [AI1 Sensor config.] (OOA1-) [AI1 Configuration] (LCA1-) [AI1 Sensor Config.] (LCS1-) [AI1 Sensor config.] (SIF1-) [AI1 Sensor Config.] (SOA1-) [AI1 Sensor Config.] (WOA1-) [AI1 Sensor Config.] (PFA1-) | 621
AI1K | AI1 Highest Process | 16#11A0 = 4512 | 16#200F/D | 16#77/01/71 = 119/01/113 | - | Configuration and settings | R/WS | INT (Signed16) | 1 | 0 | -32767 ... 32767 | [AI1 Highest Process] (AI1 ) | [AI1 sensor config.] (ICA1-) [AI1 Sensor Config.] (OCA1-) [AI1 sensor config.] (IF1-) [AI1 sensor config.] (HIF1-) [AI1 Installation Flow] (FIF1-) [AI1 Sensor Config.] (LF1-) [AI1 Sensor Config.] (bIF1-) [AI1 Configuration] (LIF1-) [AI1 Sensor config.] (PF1-) [AI1 Sensor config.] (nPF1-) [AI1 sensor config.] (IPA1-) [AI1 Configuration] (PPA1-) [AI1 Sensor config.] (OOA1-) [AI1 Configuration] (LCA1-) [AI1 Sensor Config.] (LCS1-) [AI1 Sensor config.] (SIF1-) [AI1 Sensor Config.] (SOA1-) [AI1 Sensor Config.] (WOA1-) [AI1 Sensor Config.] (PFA1-) | 622
AI2I |  | 16#1467 = 5223 | 16#2016/18 | 16#7B/01/18 = 123/01/24 | - | Measurement parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767 |  |  | 623
AI2J | AI2 Lowest Process | 16#1197 = 4503 | 16#200F/4 | 16#77/01/68 = 119/01/104 | - | Configuration and settings | R/WS | INT (Signed16) | 1 | 0 | -32767 ... 32767 | [AI2 Lowest Process] (AI2J) | [AI2 sensor config.] (ICA2-) [AI2 Sensor Config.] (OCA2-) [AI2 sensor config.] (IF2-) [AI2 sensor config.] (HIF2-) [AI2 Installation Flow] (FIF2-) [AI2 Sensor Config.] (LF2-) [AI2 Sensor Config.] (bIF2-) [AI2 Configuration] (LIF2-) [AI2 Sensor config.] (PF2-) [AI2 Sensor config.] (nPF2-) [AI2 sensor config.] (IPA2-) [AI2 Configuration] (PPA2-) [AI2 Sensor config.] (OOA2-) [AI2 Configuration] (LCA2-) [AI2 Sensor Config.] (LCS2-) [AI2 Sensor config.] (SIF2-) [AI2 Sensor Config.] (SOA2-) [AI2 Sensor Config.] (WOA2-) [AI2 Sensor Config.] (PFA2-) | 624
AI2K | AI2 Highest Process | 16#11A1 = 4513 | 16#200F/E | 16#77/01/72 = 119/01/114 | - | Configuration and settings | R/WS | INT (Signed16) | 1 | 0 | -32767 ... 32767 | [AI2 Highest Process] (AI2 ) | [AI2 sensor config.] (ICA2-) [AI2 Sensor Config.] (OCA2-) [AI2 sensor config.] (IF2-) [AI2 sensor config.] (HIF2-) [AI2 Installation Flow] (FIF2-) [AI2 Sensor Config.] (LF2-) [AI2 Sensor Config.] (bIF2-) [AI2 Configuration] (LIF2-) [AI2 Sensor config.] (PF2-) [AI2 Sensor config.] (nPF2-) [AI2 sensor config.] (IPA2-) [AI2 Configuration] (PPA2-) [AI2 Sensor config.] (OOA2-) [AI2 Configuration] (LCA2-) [AI2 Sensor Config.] (LCS2-) [AI2 Sensor config.] (SIF2-) [AI2 Sensor Config.] (SOA2-) [AI2 Sensor Config.] (WOA2-) [AI2 Sensor Config.] (PFA2-) | 625
AI3I |  | 16#1468 = 5224 | 16#2016/19 | 16#7B/01/19 = 123/01/25 | - | Measurement parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767 |  |  | 626
AI3J | AI3 Lowest Process | 16#1198 = 4504 | 16#200F/5 | 16#77/01/69 = 119/01/105 | - | Configuration and settings | R/WS | INT (Signed16) | 1 | 0 | -32767 ... 32767 | [AI3 Lowest Process] (AI3J) | [AI3 sensor config.] (ICA3-) [AI3 Sensor Config.] (OCA3-) [AI3 sensor config.] (IF3-) [AI3 sensor config.] (HIF3-) [AI3 Installation Flow] (FIF3-) [AI3 Sensor Config.] (LF3-) [AI3 Sensor Config.] (bIF3-) [AI3 Configuration] (LIF3-) [AI3 Sensor config.] (PF3-) [AI3 Sensor config.] (nPF3-) [AI3 sensor config.] (IPA3-) [AI3 Configuration] (PPA3-) [AI3 Sensor config.] (OOA3-) [AI3 Configuration] (LCA3-) [AI3 Sensor Config.] (LCS3-) [AI3 Sensor config.] (SIF3-) [AI3 Sensor Config.] (SOA3-) [AI3 Sensor Config.] (WOA3-) [AI3 Sensor Config.] (PFA3-) | 627
AI3K | AI3 Highest Process | 16#11A2 = 4514 | 16#200F/F | 16#77/01/73 = 119/01/115 | - | Configuration and settings | R/WS | INT (Signed16) | 1 | 0 | -32767 ... 32767 | [AI3 Highest Process] (AI3 ) | [AI3 sensor config.] (ICA3-) [AI3 Sensor Config.] (OCA3-) [AI3 sensor config.] (IF3-) [AI3 sensor config.] (HIF3-) [AI3 Installation Flow] (FIF3-) [AI3 Sensor Config.] (LF3-) [AI3 Sensor Config.] (bIF3-) [AI3 Configuration] (LIF3-) [AI3 Sensor config.] (PF3-) [AI3 Sensor config.] (nPF3-) [AI3 sensor config.] (IPA3-) [AI3 Configuration] (PPA3-) [AI3 Sensor config.] (OOA3-) [AI3 Configuration] (LCA3-) [AI3 Sensor Config.] (LCS3-) [AI3 Sensor config.] (SIF3-) [AI3 Sensor Config.] (SOA3-) [AI3 Sensor Config.] (WOA3-) [AI3 Sensor Config.] (PFA3-) | 628
AI4C | AI4 | 16#147D = 5245 | 16#2016/2E | 16#7B/01/2E = 123/01/46 | - | I/O parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [AI4] (AI4C) | [Display] (SUP-) | 629
AI4E | AI4 X Interm. point | 16#1171 = 4465 | 16#200E/42 | 16#77/01/42 = 119/01/66 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [AI4 X Interm. point] (AI4E) | [AI4 configuration] (AI4-) | 630
AI4F | AI4 filter | 16#1167 = 4455 | 16#200E/38 | 16#77/01/38 = 119/01/56 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 10.00 s | [AI4 filter] (AI4F) | [AI4 configuration] (AI4-) | 631
AI4I |  | 16#1469 = 5225 | 16#2016/1A | 16#7B/01/1A = 123/01/26 | - | Measurement parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767 |  |  | 632
AI4J | AI4 Lowest Process | 16#1199 = 4505 | 16#200F/6 | 16#77/01/6A = 119/01/106 | - | Configuration and settings | R/WS | INT (Signed16) | 1 | 0 | -32767 ... 32767 | [AI4 Lowest Process] (AI4J) | [AI4 sensor config.] (ICA4-) [AI4 Sensor Config.] (OCA4-) [AI4 sensor config.] (IF4-) [AI4 sensor config.] (HIF4-) [AI4 Installation Flow] (FIF4-) [AI4 Sensor Config.] (LF4-) [AI4 Sensor Config.] (bIF4-) [AI4 Configuration] (LIF4-) [AI4 Sensor config.] (PF4-) [AI4 Sensor config.] (nPF4-) [AI4 sensor config.] (IPA4-) [AI4 Configuration] (PPA4-) [AI4 Sensor config.] (OOA4-) [AI4 Configuration] (LCA4-) [AI4 Sensor Config.] (LCS4-) [AI4 Sensor config.] (SIF4-) [AI4 Sensor Config.] (SOA4-) [AI4 Sensor Config.] (WOA4-) [AI4 Sensor Config.] (PFA4-) | 633
AI4K | AI4 Highest Process | 16#11A3 = 4515 | 16#200F/10 | 16#77/01/74 = 119/01/116 | - | Configuration and settings | R/WS | INT (Signed16) | 1 | 0 | -32767 ... 32767 | [AI4 Highest Process] (AI4 ) | [AI4 sensor config.] (ICA4-) [AI4 Sensor Config.] (OCA4-) [AI4 sensor config.] (IF4-) [AI4 sensor config.] (HIF4-) [AI4 Installation Flow] (FIF4-) [AI4 Sensor Config.] (LF4-) [AI4 Sensor Config.] (bIF4-) [AI4 Configuration] (LIF4-) [AI4 Sensor config.] (PF4-) [AI4 Sensor config.] (nPF4-) [AI4 sensor config.] (IPA4-) [AI4 Configuration] (PPA4-) [AI4 Sensor config.] (OOA4-) [AI4 Configuration] (LCA4-) [AI4 Sensor Config.] (LCS4-) [AI4 Sensor config.] (SIF4-) [AI4 Sensor Config.] (SOA4-) [AI4 Sensor Config.] (WOA4-) [AI4 Sensor Config.] (PFA4-) | 634
AI4R |  | 16#1473 = 5235 | 16#2016/24 | 16#7B/01/24 = 123/01/36 | - | I/O parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767 |  |  | 635
AI4S | AI4 Y Interm.point | 16#117B = 4475 | 16#200E/4C | 16#77/01/4C = 119/01/76 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [AI4 Y Interm.point] (AI4S) | [AI4 configuration] (AI4-) | 636
AI4T | AI4 Type | 16#1135 = 4405 | 16#200E/6 | 16#77/01/06 = 119/01/06 | AIOT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Current] (0A) | - | [AI4 Type] (AI4t) | [Feedback] (Fdb-) | 637
AI5C | AI5 | 16#147E = 5246 | 16#2016/2F | 16#7B/01/2F = 123/01/47 | - | I/O parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [AI5] (AI5C) | [Display] (SUP-) | 638
AI5E | AI5 X Interm. point | 16#1172 = 4466 | 16#200E/43 | 16#77/01/43 = 119/01/67 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [AI5 X Interm. point] (AI5E) | [AI5 configuration] (AI5-) | 639
AI5F | AI5 filter | 16#1168 = 4456 | 16#200E/39 | 16#77/01/39 = 119/01/57 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 10.00 s | [AI5 filter] (AI5F) | [AI5 configuration] (AI5-) | 640
AI5I |  | 16#146A = 5226 | 16#2016/1B | 16#7B/01/1B = 123/01/27 | - | Measurement parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767 |  |  | 641
AI5J | AI5 Lowest Process | 16#119A = 4506 | 16#200F/7 | 16#77/01/6B = 119/01/107 | - | Configuration and settings | R/WS | INT (Signed16) | 1 | 0 | -32767 ... 32767 | [AI5 Lowest Process] (AI5J) | [AI5 sensor config.] (ICA5-) [AI5 Sensor Config.] (OCA5-) [AI5 sensor config.] (IF5-) [AI5 sensor config.] (HIF5-) [AI5 Installation Flow] (FIF5-) [AI5 Sensor Config.] (LF5-) [AI5 Sensor Config.] (bIF5-) [AI5 Configuration] (LIF5-) [AI5 Sensor config.] (PF5-) [AI5 Sensor config.] (nPF5-) [AI5 sensor config.] (IPA5-) [AI5 Configuration] (PPA5-) [AI5 Sensor config.] (OOA5-) [AI5 Configuration] (LCA5-) [AI5 Sensor Config.] (LCS5-) [AI5 Sensor config.] (SIF5-) [AI5 Sensor Config.] (SOA5-) [AI5 Sensor Config.] (WOA5-) [AI5 Sensor Config.] (PFA5-) | 642
AI5K | AI5 Highest Process | 16#11A4 = 4516 | 16#200F/11 | 16#77/01/75 = 119/01/117 | - | Configuration and settings | R/WS | INT (Signed16) | 1 | 0 | -32767 ... 32767 | [AI5 Highest Process] (AI5 ) | [AI5 sensor config.] (ICA5-) [AI5 Sensor Config.] (OCA5-) [AI5 sensor config.] (IF5-) [AI5 sensor config.] (HIF5-) [AI5 Installation Flow] (FIF5-) [AI5 Sensor Config.] (LF5-) [AI5 Sensor Config.] (bIF5-) [AI5 Configuration] (LIF5-) [AI5 Sensor config.] (PF5-) [AI5 Sensor config.] (nPF5-) [AI5 sensor config.] (IPA5-) [AI5 Configuration] (PPA5-) [AI5 Sensor config.] (OOA5-) [AI5 Configuration] (LCA5-) [AI5 Sensor Config.] (LCS5-) [AI5 Sensor config.] (SIF5-) [AI5 Sensor Config.] (SOA5-) [AI5 Sensor Config.] (WOA5-) [AI5 Sensor Config.] (PFA5-) | 643
AI5R |  | 16#1474 = 5236 | 16#2016/25 | 16#7B/01/25 = 123/01/37 | - | I/O parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767 |  |  | 644
AI5S | AI5 Y Interm.point | 16#117C = 4476 | 16#200E/4D | 16#77/01/4D = 119/01/77 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [AI5 Y Interm.point] (AI5S) | [AI5 configuration] (AI5-) | 645
AI5T | AI5 Type | 16#1136 = 4406 | 16#200E/7 | 16#77/01/07 = 119/01/07 | AIOT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Current] (0A) | - | [AI5 Type] (AI5t) | [Feedback] (Fdb-) | 646
AIC1 | AIV1 Channel Assign | 16#14A2 = 5282 | 16#2016/53 | 16#7B/01/53 = 123/01/83 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Configured] (nO) | - | [AIV1 Channel Assign] (AIC1) | [Virtual AI1] (AU1-) | 647
AO1I |  | 16#1483 = 5251 | 16#2016/34 | 16#7B/01/34 = 123/01/52 | - | I/O parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767 |  |  | 648
AO2 | AQ2 assignment | 16#139E = 5022 | 16#2014/17 | 16#7A/01/17 = 122/01/23 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Motor Current] (OCr) | - | [AQ2 assignment] (AO2) | [AQ2 configuration] (AO2-) | 649
AO2C | AQ2 | 16#1498 = 5272 | 16#2016/49 | 16#7B/01/49 = 123/01/73 | - | I/O parameters | R/W | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [AQ2] (AO2C) | [Display] (SUP-) | 650
AO2F | AQ2 Filter | 16#1204 = 4612 | 16#2010/D | 16#78/01/0D = 120/01/13 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 10.00 s | [AQ2 Filter] (AO2F) | [AQ2 configuration] (AO2-) | 651
AO2I |  | 16#1484 = 5252 | 16#2016/35 | 16#7B/01/35 = 123/01/53 | - | I/O parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767 |  |  | 652
AO2R |  | 16#148E = 5262 | 16#2016/3F | 16#7B/01/3F = 123/01/63 | - | I/O parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767 |  |  | 653
AO2T | AQ2 Type | 16#11FA = 4602 | 16#2010/3 | 16#78/01/03 = 120/01/03 | AIOT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Current] (0A) | - | [AQ2 Type] (AO2t) | [AQ2 configuration] (AO2-) | 654
AOH2 | AQ2 max output | 16#122C = 4652 | 16#2010/35 | 16#78/01/35 = 120/01/53 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mA | 20.0 mA | 0.0 mA ... 20.0 mA | [AQ2 max output] (AOH2) | [AQ2 configuration] (AO2-) | 655
AOL2 | AQ2 min output | 16#1222 = 4642 | 16#2010/2B | 16#78/01/2B = 120/01/43 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mA | 0.0 mA | 0.0 mA ... 20.0 mA | [AQ2 min output] (AOL2) | [AQ2 configuration] (AO2-) | 656
APPS | Application state | 16#3E6C = 15980 | 16#2081/51 | 16#B0/01/B5 = 176/01/181 | APPS | Status parameters | R | WORD (Enumeration) | - |  | - | [Application state] (APPS) | [Control] (Ctr-) [Application Parameters] (APr-) [Display] (SUP-) | 657
ASH2 | Scaling AQ2 max | 16#1240 = 4672 | 16#2010/49 | 16#78/01/49 = 120/01/73 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 % | 100.0 % | 0.0 % ... 100.0 % | [Scaling AQ2 max] (ASH2) | [AQ2 configuration] (AO2-) | 658
ASL2 | Scaling AQ2 min | 16#1236 = 4662 | 16#2010/3F | 16#78/01/3F = 120/01/63 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 % | 0.0 % | 0.0 % ... 100.0 % | [Scaling AQ2 min] (ASL2) | [AQ2 configuration] (AO2-) | 659
ASLC | Sleep Condition | 16#2E05 = 11781 | 16#2057/52 | 16#9B/01/B6 = 155/01/182 | - | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [Sleep Condition] (ASLC) | [Settings] (SEt-) [Advanced sleep check] (AdS-) | 660
ASLD | Sleep Check Delay | 16#2E06 = 11782 | 16#2057/53 | 16#9B/01/B7 = 155/01/183 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | 20 s | 0 s ... 9999 s | [Sleep Check Delay] (ASLd) | [Settings] (SEt-) [Advanced sleep check] (AdS-) | 661
ASLM | Sleep Mode | 16#2E04 = 11780 | 16#2057/51 | 16#9B/01/B5 = 155/01/181 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Sleep Mode] (ASLM) | [Advanced sleep check] (AdS-) | 662
ASLR | Check Sleep Ref spd | 16#2E07 = 11783 | 16#2057/54 | 16#9B/01/B8 = 155/01/184 | - | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [Check Sleep Ref spd] (ASLr) | [Settings] (SEt-) [Advanced sleep check] (AdS-) | 663
CAR | Warning Clearing | 16#3F98 = 16280 | 16#2084/51 | 16#B2/01/51 = 178/01/81 | CAR | Configuration and settings | R/W | WORD (Enumeration) | - | [No Warning Clearing] (nO) | - | [Warning Clearing] (CAr) | [Customer events] (CUEU-) | 664
CASH | Money Saved | 16#2A36 = 10806 | 16#204E/7 | 16#97/01/07 = 151/01/07 |  | Actual values parameters | R | UINT (Unsigned32) | - |  | - | [Money Saved] (CASH) | [Energy Saving] (ESA-) | 665
CC1 | Time counter 1 | 16#3F84 = 16260 | 16#2084/3D | 16#B2/01/3D = 178/01/61 |  | Actual values parameters | R | UINT (Unsigned32) | - |  | - | [Time counter 1] (CC1) | [Customer event 1] (CE1-) | 666
CC2 | Time counter 2 | 16#3F86 = 16262 | 16#2084/3F | 16#B2/01/3F = 178/01/63 |  | Actual values parameters | R | UINT (Unsigned32) | - |  | - | [Time counter 2] (CC2) | [Customer event 2] (CE2-) | 667
CC3 | Time counter 3 | 16#3F88 = 16264 | 16#2084/41 | 16#B2/01/41 = 178/01/65 |  | Actual values parameters | R | UINT (Unsigned32) | - |  | - | [Time counter 3] (CC3) | [Customer event 3] (CE3-) | 668
CC4 | Time counter 4 | 16#3F8A = 16266 | 16#2084/43 | 16#B2/01/43 = 178/01/67 |  | Actual values parameters | R | UINT (Unsigned32) | - |  | - | [Time counter 4] (CC4) | [Customer event 4] (CE4-) | 669
CC5 | Time counter 5 | 16#3F8C = 16268 | 16#2084/45 | 16#B2/01/45 = 178/01/69 |  | Actual values parameters | R | UINT (Unsigned32) | - |  | - | [Time counter 5] (CC5) | [Customer event 5] (CE5-) | 670
CCA1 | Config Warning 1 | 16#3F48 = 16200 | 16#2084/1 | 16#B2/01/01 = 178/01/01 | CCA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Configured] (nO) | - | [Config Warning 1] (CCA1) | [Customer event 1] (CE1-) | 671
CCA2 | Config Warning 2 | 16#3F49 = 16201 | 16#2084/2 | 16#B2/01/02 = 178/01/02 | CCA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Configured] (nO) | - | [Config Warning 2] (CCA2) | [Customer event 2] (CE2-) | 672
CCA3 | Config Warning 3 | 16#3F4A = 16202 | 16#2084/3 | 16#B2/01/03 = 178/01/03 | CCA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Configured] (nO) | - | [Config Warning 3] (CCA3) | [Customer event 3] (CE3-) | 673
CCA4 | Config Warning 4 | 16#3F4B = 16203 | 16#2084/4 | 16#B2/01/04 = 178/01/04 | CCA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Configured] (nO) | - | [Config Warning 4] (CCA4) | [Customer event 4] (CE4-) | 674
CCA5 | Config Warning 5 | 16#3F4C = 16204 | 16#2084/5 | 16#B2/01/05 = 178/01/05 | CCA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Configured] (nO) | - | [Config Warning 5] (CCA5) | [Customer event 5] (CE5-) | 675
CCL1 | Counter limit 1 | 16#3F70 = 16240 | 16#2084/29 | 16#B2/01/29 = 178/01/41 |  | Configuration and settings | R/WS | UINT (Unsigned32) | - | 0 s | - | [Counter limit 1] (CCL1) | [Customer event 1] (CE1-) | 676
CCL2 | Counter limit 2 | 16#3F72 = 16242 | 16#2084/2B | 16#B2/01/2B = 178/01/43 |  | Configuration and settings | R/WS | UINT (Unsigned32) | - | 0 s | - | [Counter limit 2] (CCL2) | [Customer event 2] (CE2-) | 677
CCL3 | Counter limit 3 | 16#3F74 = 16244 | 16#2084/2D | 16#B2/01/2D = 178/01/45 |  | Configuration and settings | R/WS | UINT (Unsigned32) | - | 0 s | - | [Counter limit 3] (CCL3) | [Customer event 3] (CE3-) | 678
CCL4 | Counter limit 4 | 16#3F76 = 16246 | 16#2084/2F | 16#B2/01/2F = 178/01/47 |  | Configuration and settings | R/WS | UINT (Unsigned32) | - | 0 s | - | [Counter limit 4] (CCL4) | [Customer event 4] (CE4-) | 679
CCL5 | Counter limit 5 | 16#3F78 = 16248 | 16#2084/31 | 16#B2/01/31 = 178/01/49 |  | Configuration and settings | R/WS | UINT (Unsigned32) | - | 0 s | - | [Counter limit 5] (CCL5) | [Customer event 5] (CE5-) | 680
CCS1 | Counter Source 1 | 16#3F52 = 16210 | 16#2084/B | 16#B2/01/0B = 178/01/11 | CCS | Configuration and settings | R/WS | WORD (Enumeration) | - | [Drv in run state] (2) | - | [Counter Source 1] (CCS1) | [Customer event 1] (CE1-) | 681
CCS2 | Counter Source 2 | 16#3F53 = 16211 | 16#2084/C | 16#B2/01/0C = 178/01/12 | CCS | Configuration and settings | R/WS | WORD (Enumeration) | - | [Drv in run state] (2) | - | [Counter Source 2] (CCS2) | [Customer event 2] (CE2-) | 682
CCS3 | Counter Source 3 | 16#3F54 = 16212 | 16#2084/D | 16#B2/01/0D = 178/01/13 | CCS | Configuration and settings | R/WS | WORD (Enumeration) | - | [Drv in run state] (2) | - | [Counter Source 3] (CCS3) | [Customer event 3] (CE3-) | 683
CCS4 | Counter Source 4 | 16#3F55 = 16213 | 16#2084/E | 16#B2/01/0E = 178/01/14 | CCS | Configuration and settings | R/WS | WORD (Enumeration) | - | [Drv in run state] (2) | - | [Counter Source 4] (CCS4) | [Customer event 4] (CE4-) | 684
CCS5 | Counter Source 5 | 16#3F56 = 16214 | 16#2084/F | 16#B2/01/0F = 178/01/15 | CCS | Configuration and settings | R/WS | WORD (Enumeration) | - | [Drv in run state] (2) | - | [Counter Source 5] (CCS5) | [Customer event 5] (CE5-) | 685
CDT1 |  | 16#3F5C = 16220 | 16#2084/15 | 16#B2/01/15 = 178/01/21 |  | Configuration and settings | R/W | UINT (Unsigned32) | - | 2162688 | - |  |  | 686
CDT2 |  | 16#3F5E = 16222 | 16#2084/17 | 16#B2/01/17 = 178/01/23 |  | Configuration and settings | R/W | UINT (Unsigned32) | - | 2162688 | - |  |  | 687
CDT3 |  | 16#3F60 = 16224 | 16#2084/19 | 16#B2/01/19 = 178/01/25 |  | Configuration and settings | R/W | UINT (Unsigned32) | - | 2162688 | - |  |  | 688
CDT4 |  | 16#3F62 = 16226 | 16#2084/1B | 16#B2/01/1B = 178/01/27 |  | Configuration and settings | R/W | UINT (Unsigned32) | - | 2162688 | - |  |  | 689
CDT5 |  | 16#3F64 = 16228 | 16#2084/1D | 16#B2/01/1D = 178/01/29 |  | Configuration and settings | R/W | UINT (Unsigned32) | - | 2162688 | - |  |  | 690
CHT | Flow Lim Thd Active | 16#38B0 = 14512 | 16#2073/D | 16#A9/01/71 = 169/01/113 | - | Configuration and settings | R/W | INT (Signed16) | (call FlowRateUnitSelection [SUFR]) | (call FlowRateUnitSelection [SUFR]) | (call FlowRateUnitSelection [SUFR]) ... (call FlowRateUnitSelection [SUFR]) | [Flow Lim Thd Active] (CHt) | [Settings] (SEt-) | 691
CMP9 | Cmd word | 16#1C47 = 7239 | 16#202A/28 | 16#85/01/28 = 133/01/40 | CMP9 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 692
CMPA | Cmd word | 16#1DCE = 7630 | 16#202E/1F | 16#87/01/1F = 135/01/31 | CMPA | History parameters | R | WORD (BitString16) | - |  | - |  |  | 693
CMPB | Cmd word | 16#1DCF = 7631 | 16#202E/20 | 16#87/01/20 = 135/01/32 | CMPB | History parameters | R | WORD (BitString16) | - |  | - |  |  | 694
CMPC | CMD word | 16#1DD0 = 7632 | 16#202E/21 | 16#87/01/21 = 135/01/33 | CMPC | History parameters | R | WORD (BitString16) | - |  | - |  |  | 695
CMPD | CMD word | 16#1DD1 = 7633 | 16#202E/22 | 16#87/01/22 = 135/01/34 | CMPD | History parameters | R | WORD (BitString16) | - |  | - |  |  | 696
CMPE | CMD word | 16#1DD2 = 7634 | 16#202E/23 | 16#87/01/23 = 135/01/35 | CMPE | History parameters | R | WORD (BitString16) | - |  | - |  |  | 697
CMPF | CMD word | 16#1DD3 = 7635 | 16#202E/24 | 16#87/01/24 = 135/01/36 | CMPF | History parameters | R | WORD (BitString16) | - |  | - |  |  | 698
CO2S | Co2 Saved | 16#2A38 = 10808 | 16#204E/9 | 16#97/01/09 = 151/01/09 |  | Actual values parameters | R | UINT (Unsigned32) | - |  | - | [Co2 Saved] (CO2S) | [Energy Saving] (ESA-) | 699
CRH1 | AI1 Max Value | 16#115A = 4442 | 16#200E/2B | 16#77/01/2B = 119/01/43 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mA | 20.0 mA | 0.0 mA ... 20.0 mA | [AI1 Max Value] (CrH1) | [Feedback] (Fdb-) | 700
CRH2 | AI2 Max Value | 16#115B = 4443 | 16#200E/2C | 16#77/01/2C = 119/01/44 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mA | 20.0 mA | 0.0 mA ... 20.0 mA | [AI2 Max Value] (CrH2) | [Feedback] (Fdb-) | 701
CRH4 | AI4 Max Value | 16#115D = 4445 | 16#200E/2E | 16#77/01/2E = 119/01/46 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mA | 20.0 mA | 0.0 mA ... 20.0 mA | [AI4 Max Value] (CrH4) | [Feedback] (Fdb-) | 702
CRH5 | AI5 Max Value | 16#115E = 4446 | 16#200E/2F | 16#77/01/2F = 119/01/47 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mA | 20.0 mA | 0.0 mA ... 20.0 mA | [AI5 Max Value] (CrH5) | [Feedback] (Fdb-) | 703
CRL1 | AI1 Min. Value | 16#1150 = 4432 | 16#200E/21 | 16#77/01/21 = 119/01/33 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mA | 0.0 mA | 0.0 mA ... 20.0 mA | [AI1 Min. Value] (CrL1) | [Feedback] (Fdb-) | 704
CRL2 | AI2 Min. Value | 16#1151 = 4433 | 16#200E/22 | 16#77/01/22 = 119/01/34 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mA | 0.0 mA | 0.0 mA ... 20.0 mA | [AI2 Min. Value] (CrL2) | [Feedback] (Fdb-) | 705
CRL4 | AI4 Min. Value | 16#1153 = 4435 | 16#200E/24 | 16#77/01/24 = 119/01/36 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mA | 0.0 mA | 0.0 mA ... 20.0 mA | [AI4 Min. Value] (CrL4) | [Feedback] (Fdb-) | 706
CRL5 | AI5 Min. Value | 16#1154 = 4436 | 16#200E/25 | 16#77/01/25 = 119/01/37 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mA | 0.0 mA | 0.0 mA ... 20.0 mA | [AI5 Min. Value] (CrL5) | [Feedback] (Fdb-) | 707
CRP9 |  | 16#1C83 = 7299 | 16#202A/64 | 16#85/01/64 = 133/01/100 | CRP9 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 708
CRPA |  | 16#1E0A = 7690 | 16#202E/5B | 16#87/01/5B = 135/01/91 | CRPA | History parameters | R | WORD (BitString16) | - |  | - |  |  | 709
CRPB |  | 16#1E0B = 7691 | 16#202E/5C | 16#87/01/5C = 135/01/92 | CRPB | History parameters | R | WORD (BitString16) | - |  | - |  |  | 710
CRPC |  | 16#1E0C = 7692 | 16#202E/5D | 16#87/01/5D = 135/01/93 | CRPC | History parameters | R | WORD (BitString16) | - |  | - |  |  | 711
CRPD |  | 16#1E0D = 7693 | 16#202E/5E | 16#87/01/5E = 135/01/94 | CRPD | History parameters | R | WORD (BitString16) | - |  | - |  |  | 712
CRPE |  | 16#1E0E = 7694 | 16#202E/5F | 16#87/01/5F = 135/01/95 | CRPE | History parameters | R | WORD (BitString16) | - |  | - |  |  | 713
CRPF |  | 16#1E0F = 7695 | 16#202E/60 | 16#87/01/60 = 135/01/96 | CRPF | History parameters | R | WORD (BitString16) | - |  | - |  |  | 714
CTDL | Low I Threshold | 16#2B02 = 11010 | 16#2050/B | 16#98/01/0B = 152/01/11 | - | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | Depends of rating | Depends of rating | [Low I Threshold] (CtdL) | [Threshold reached] (tHrE-) [Settings] (SEt-) | 715
CVHS | Check Valve Spd 2 | 16#2352 = 9042 | 16#203C/2B | 16#8E/01/2B = 142/01/43 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [Check Valve Spd 2] (CUHS) | [Settings] (SEt-) [Pump start stop] (PSt-) | 716
CVLS | Check Valve Spd 1 | 16#2353 = 9043 | 16#203C/2C | 16#8E/01/2C = 142/01/44 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [Check Valve Spd 1] (CULS) | [Settings] (SEt-) [Pump start stop] (PSt-) | 717
D11D | DQ11 actv delay | 16#10BB = 4283 | 16#200C/54 | 16#76/01/54 = 118/01/84 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [DQ11 actv delay] (d11d) | [DQ11 Configuration] (dO11-) | 718
D11H | DQ11 hold delay | 16#10B1 = 4273 | 16#200C/4A | 16#76/01/4A = 118/01/74 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [DQ11 hold delay] (d11H) | [DQ11 Configuration] (dO11-) | 719
D11S | DQ11 status | 16#10A7 = 4263 | 16#200C/40 | 16#76/01/40 = 118/01/64 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [1] (POS) | - | [DQ11 status] (d11S) | [DQ11 Configuration] (dO11-) | 720
D12D | DQ12 actv delay | 16#10BC = 4284 | 16#200C/55 | 16#76/01/55 = 118/01/85 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [DQ12 actv delay] (d12d) | [DQ12 Configuration] (dO12-) | 721
D12H | DQ12 hold delay | 16#10B2 = 4274 | 16#200C/4B | 16#76/01/4B = 118/01/75 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [DQ12 hold delay] (d12H) | [DQ12 Configuration] (dO12-) | 722
D12S | DQ12 status | 16#10A8 = 4264 | 16#200C/41 | 16#76/01/41 = 118/01/65 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [1] (POS) | - | [DQ12 status] (d12S) | [DQ12 Configuration] (dO12-) | 723
DECS | Final Dec. Ramp | 16#2354 = 9044 | 16#203C/2D | 16#8E/01/2D = 142/01/45 | - | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | [No] (nO) | Refer to programming manual | [Final Dec. Ramp] (dECS) | [Settings] (SEt-) [Pump start stop] (PSt-) | 724
DECV | Dec. Check Valve | 16#2351 = 9041 | 16#203C/2A | 16#8E/01/2A = 142/01/42 | - | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | [No] (nO) | Refer to programming manual | [Dec. Check Valve] (dECU) | [Settings] (SEt-) [Pump start stop] (PSt-) | 725
DFL | Flow. Limit Dec. | 16#38B2 = 14514 | 16#2073/F | 16#A9/01/73 = 169/01/115 | - | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | Refer to programming manual | [Flow. Limit Dec.] (dFL) | [Settings] (SEt-) | 726
DM0 |  | 16#1C8E = 7310 | 16#202B/B | 16#85/01/6F = 133/01/111 | - | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 727
DM1 |  | 16#1C8F = 7311 | 16#202B/C | 16#85/01/70 = 133/01/112 | - | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 728
DM2 |  | 16#1C90 = 7312 | 16#202B/D | 16#85/01/71 = 133/01/113 | - | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 729
DM3 |  | 16#1C91 = 7313 | 16#202B/E | 16#85/01/72 = 133/01/114 | - | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 730
DM4 |  | 16#1C92 = 7314 | 16#202B/F | 16#85/01/73 = 133/01/115 | - | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 731
DM5 |  | 16#1C93 = 7315 | 16#202B/10 | 16#85/01/74 = 133/01/116 | - | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 732
DM6 |  | 16#1C94 = 7316 | 16#202B/11 | 16#85/01/75 = 133/01/117 | - | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 733
DM7 |  | 16#1C95 = 7317 | 16#202B/12 | 16#85/01/76 = 133/01/118 | - | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 734
DM8 |  | 16#1C96 = 7318 | 16#202B/13 | 16#85/01/77 = 133/01/119 | - | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 735
DM9 |  | 16#1C97 = 7319 | 16#202B/14 | 16#85/01/78 = 133/01/120 | - | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 736
DMA |  | 16#1E1E = 7710 | 16#202F/B | 16#87/01/6F = 135/01/111 | - | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 737
DMB |  | 16#1E1F = 7711 | 16#202F/C | 16#87/01/70 = 135/01/112 | - | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 738
DMC |  | 16#1E20 = 7712 | 16#202F/D | 16#87/01/71 = 135/01/113 | - | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 739
DMD |  | 16#1E21 = 7713 | 16#202F/E | 16#87/01/72 = 135/01/114 | - | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 740
DME |  | 16#1E22 = 7714 | 16#202F/F | 16#87/01/73 = 135/01/115 | - | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 741
DMF |  | 16#1E23 = 7715 | 16#202F/10 | 16#87/01/74 = 135/01/116 | - | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 742
DO11 | DQ11 assignment | 16#13A9 = 5033 | 16#2014/22 | 16#7A/01/22 = 122/01/34 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Assigned] (nO) | - | [DQ11 assignment] (dO11) | [DQ11 Configuration] (dO11-) | 743
DO12 | DQ12 assignment | 16#13AA = 5034 | 16#2014/23 | 16#7A/01/23 = 122/01/35 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Assigned] (nO) | - | [DQ12 assignment] (dO12) | [DQ12 Configuration] (dO12-) | 744
DP9 |  | 16#1C29 = 7209 | 16#202A/A | 16#85/01/0A = 133/01/10 | LFT | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 745
DPA |  | 16#1DB0 = 7600 | 16#202E/1 | 16#87/01/01 = 135/01/01 | LFT | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 746
DPB |  | 16#1DB1 = 7601 | 16#202E/2 | 16#87/01/02 = 135/01/02 | LFT | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 747
DPC |  | 16#1DB2 = 7602 | 16#202E/3 | 16#87/01/03 = 135/01/03 | LFT | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 748
DPD |  | 16#1DB3 = 7603 | 16#202E/4 | 16#87/01/04 = 135/01/04 | LFT | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 749
DPE |  | 16#1DB4 = 7604 | 16#202E/5 | 16#87/01/05 = 135/01/05 | LFT | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 750
DPF |  | 16#1DB5 = 7605 | 16#202E/6 | 16#87/01/06 = 135/01/06 | LFT | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 751
DRT | Dual rating | 16#0BC2 = 3010 | 16#2000/B | 16#70/01/0B = 112/01/11 | DRT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Normal Duty] (nOrMAL) | - | [Dual rating] (drt) | [Motor parameters] (MPA-) | 752
DRYD | DryRun Error Delay | 16#3E50 = 15952 | 16#2081/35 | 16#B0/01/99 = 176/01/153 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | 5 s | 0 s ... 3600 s | [DryRun Error Delay] (drYd) | [Settings] (SEt-) [Dry run Monit] (dYr-) | 753
DRYM | DryRun Mode | 16#3E4E = 15950 | 16#2081/33 | 16#B0/01/97 = 176/01/151 | DRYM | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [DryRun Mode] (drYM) | [Dry run Monit] (dYr-) | 754
DRYR | DryRun Restart Delay | 16#3E51 = 15953 | 16#2081/36 | 16#B0/01/9A = 176/01/154 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | 60 s | 10 s ... 3600 s | [DryRun Restart Delay] (drYr) | [Settings] (SEt-) [Dry run Monit] (dYr-) | 755
DRYW | Switch Select | 16#3E4F = 15951 | 16#2081/34 | 16#B0/01/98 = 176/01/152 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Assigned] (nO) | - | [Switch Select] (drYW) | [Dry run Monit] (dYr-) | 756
DRYX | Dry Run Factor | 16#3E52 = 15954 | 16#2081/37 | 16#B0/01/9B = 176/01/155 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 90 % | 0 % ... 100 % | [Dry Run Factor] (drYX) | [Settings] (SEt-) [Dry run Monit] (dYr-) | 757
ECI | Energy Cons. Ind. | 16#3EB5 = 16053 | 16#2082/36 | 16#B1/01/36 = 177/01/54 | - | Actual values parameters | R | INT (Signed16) | (call WaterSpecificEnergyUnitSelection [SUFR]) |  | (call WaterSpecificEnergyUnitSelection [SUFR]) ... (call WaterSpecificEnergyUnitSelection [SUFR]) | [Energy Cons. Ind.] (ECI) | [Variable Speed Pump] (MPP-) [Display] (SUP-) | 758
ECO2 | CO2 ratio | 16#2A32 = 10802 | 16#204E/3 | 16#97/01/03 = 151/01/03 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.001 kg/kWh | 0.000 kg/kWh | 0.000 kg/kWh ... 65.535 kg/kWh | [CO2 ratio] (ECO2) | [Energy Saving] (ESA-) | 759
ECST | kWh Cost | 16#2A31 = 10801 | 16#204E/2 | 16#97/01/02 = 151/01/02 | - | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | Refer to programming manual | [kWh Cost] (ECSt) | [Energy Saving] (ESA-) | 760
EFY | Efficiency | 16#3EB2 = 16050 | 16#2082/33 | 16#B1/01/33 = 177/01/51 | - | Actual values parameters | R | UINT (Unsigned16) | 0.1 % |  | 0.0 % ... 100.0 % | [Efficiency] (EFY) | [Variable Speed Pump] (MPP-) [Display] (SUP-) | 761
EFYJ | Lowest Eff. | 16#3EB4 = 16052 | 16#2082/35 | 16#B1/01/35 = 177/01/53 | - | Actual values parameters | R | UINT (Unsigned16) | 0.1 % |  | 0.0 % ... 100.0 % | [Lowest Eff.] (EFYJ) | [Variable Speed Pump] (MPP-) | 762
EFYK | Highest Eff. | 16#3EB3 = 16051 | 16#2082/34 | 16#B1/01/34 = 177/01/52 | - | Actual values parameters | R | UINT (Unsigned16) | 0.1 % |  | 0.0 % ... 100.0 % | [Highest Eff.] (EFY ) | [Variable Speed Pump] (MPP-) | 763
EP9 | ETA state word | 16#1C33 = 7219 | 16#202A/14 | 16#85/01/14 = 133/01/20 | EP9 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 764
EPA | ETA state word | 16#1DBA = 7610 | 16#202E/B | 16#87/01/0B = 135/01/11 | EPA | History parameters | R | WORD (BitString16) | - |  | - |  |  | 765
EPB | ETA state word | 16#1DBB = 7611 | 16#202E/C | 16#87/01/0C = 135/01/12 | EPB | History parameters | R | WORD (BitString16) | - |  | - |  |  | 766
EPC | ETA state word | 16#1DBC = 7612 | 16#202E/D | 16#87/01/0D = 135/01/13 | EPC | History parameters | R | WORD (BitString16) | - |  | - |  |  | 767
EPD | ETA state word | 16#1DBD = 7613 | 16#202E/E | 16#87/01/0E = 135/01/14 | EPD | History parameters | R | WORD (BitString16) | - |  | - |  |  | 768
EPE | ETA state word | 16#1DBE = 7614 | 16#202E/F | 16#87/01/0F = 135/01/15 | EPE | History parameters | R | WORD (BitString16) | - |  | - |  |  | 769
EPF | ETA state word | 16#1DBF = 7615 | 16#202E/10 | 16#87/01/10 = 135/01/16 | EPF | History parameters | R | WORD (BitString16) | - |  | - |  |  | 770
EPI | Energy Perf. Ind | 16#3EB6 = 16054 | 16#2082/37 | 16#B1/01/37 = 177/01/55 | - | Actual values parameters | R | INT (Signed16) | (call NRGPerformanceUnitSelection [SUFR]) |  | (call NRGPerformanceUnitSelection [SUFR]) ... (call NRGPerformanceUnitSelection [SUFR]) | [Energy Perf. Ind] (EPI) | [Variable Speed Pump] (MPP-) [Display] (SUP-) | 771
EPRW | Acv Elc Out Pwr Estm | 16#0CDD = 3293 | 16#2002/5E | 16#71/01/5E = 113/01/94 | - | Actual values parameters | R | INT (Signed16) | Refer to programming manual |  | Depends of rating | [Acv Elc Out Pwr Estm] (EPrW) | [kWh Counters] ( WC-) [Elec Ener Output Counter] (ELO-) [Variable Speed Pump] (MPP-) [Display] (SUP-) | 772
ERR | Ethernet Error Code | 16#FB0E = 64270 |  | = | - | Fault parameters | [always] | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Ethernet Error Code] (Err) | [PROFINET DIAG] (Prn-) | 773
ESAV | Energy Saved | 16#2A34 = 10804 | 16#204E/5 | 16#97/01/05 = 151/01/05 |  | Actual values parameters | R/WS | UINT (Unsigned32) | - |  | - | [Energy Saved] (ESAU) | [Energy Saving] (ESA-) | 774
ETAD |  | 16#219B = 8603 | 16#2038/4 | 16#8C/01/04 = 140/01/04 | ETAD | Status parameters | R | WORD (BitString16) | - |  | - |  |  | 775
ETHF |  | 16#1BE0 = 7136 | 16#2029/25 | 16#84/01/89 = 132/01/137 | - | Fault parameters | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 776
ETHL | Eth Error Response | 16#1B6D = 7021 | 16#2028/16 | 16#84/01/16 = 132/01/22 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel Stop] (YES) | - | [Eth Error Response] (EtHL) | [Embedded modbus TCP] (EMtC-) [Communication Module] (COMO-) | 777
F2DL | 2 Freq. Threshold | 16#2B04 = 11012 | 16#2050/D | 16#98/01/0D = 152/01/13 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 500.0 Hz | [2 Freq. Threshold] (F2dL) | [Threshold reached] (tHrE-) [Settings] (SEt-) | 778
FPBT | Fan Operation Time | 16#0CC0 = 3264 | 16#2002/41 | 16#71/01/41 = 113/01/65 |  | Actual values parameters | R/WS | UINT (Unsigned32) | - |  | - | [Fan Operation Time] (FPbt) | [Counter Management] (ELt-) [Display] (SUP-) | 779
FEM | Flow Estimation Mode | 16#3E80 = 16000 | 16#2082/1 | 16#B1/01/01 = 177/01/01 | FEM | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Flow Estimation Mode] (FEM) | [Flow estimation] (SFE-) | 780
FLCM | Mode Selection | 16#3DE0 = 15840 | 16#2080/29 | 16#B0/01/29 = 176/01/41 | FLCM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Inactive] (nO) | - | [Mode Selection] (FLCM) | [Friction loss comp] (FLC-) | 781
FLDA | Alpha | 16#3DE1 = 15841 | 16#2080/2A | 16#B0/01/2A = 176/01/42 | - | Configuration and settings | R/W | INT (Signed16) | 0.1 | 2.0 | 0.0 ... 2.0 | [Alpha] (FLdA) | [Settings] (SEt-) [Friction loss comp] (FLC-) | 782
FLH0 | Static Compensation | 16#3DE4 = 15844 | 16#2080/2D | 16#B0/01/2D = 176/01/45 | - | Configuration and settings | R/W | INT (Signed16) | (call PressureUnitSelected [SUPR]) | (call PressureUnitSelected [SUPR]) | (call PressureUnitSelected [SUPR]) ... (call PressureUnitSelected [SUPR]) | [Static Compensation] (FLH0) | [Settings] (SEt-) [Friction loss comp] (FLC-) | 783
FLH1 | Comp. at Point 1 | 16#3DE2 = 15842 | 16#2080/2B | 16#B0/01/2B = 176/01/43 | - | Configuration and settings | R/W | INT (Signed16) | (call PressureUnitSelected [SUPR]) | (call PressureUnitSelected [SUPR]) | (call PressureUnitSelected [SUPR]) ... (call PressureUnitSelected [SUPR]) | [Comp. at Point 1] (FLH1) | [Settings] (SEt-) [Friction loss comp] (FLC-) | 784
FLM | Flow limitation Mode | 16#38B3 = 14515 | 16#2073/10 | 16#A9/01/74 = 169/01/116 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Flow limitation Mode] (FLM) | [Flow limitation] (FLM-) | 785
FLPD | Delta Pressure | 16#3DE5 = 15845 | 16#2080/2E | 16#B0/01/2E = 176/01/46 | - | Configuration and settings | R | INT (Signed16) | (call PressureUnitSelected [SUPR]) |  | (call PressureUnitSelected [SUPR]) ... (call PressureUnitSelected [SUPR]) | [Delta Pressure] (FLPd) | [Friction loss comp] (FLC-) | 786
FLQ1 | Flow at Point 1 | 16#3DE3 = 15843 | 16#2080/2C | 16#B0/01/2C = 176/01/44 | - | Configuration and settings | R/W | INT (Signed16) | (call FlowRateUnitSelection [SUFR]) | (call FlowRateUnitSelection [SUFR]) | (call FlowRateUnitSelection [SUFR]) ... (call FlowRateUnitSelection [SUFR]) | [Flow at Point 1] (FLq1) | [Settings] (SEt-) [Friction loss comp] (FLC-) | 787
FS1A | Inst. Flow Assign. | 16#3D57 = 15703 | 16#207F/4 | 16#AF/01/68 = 175/01/104 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Configured] (nO) | - | [Inst. Flow Assign.] (FS1A) | [Sensors Assignment] (SSC-) | 788
FS1C | Total Quantity | 16#3D65 = 15717 | 16#207F/12 | 16#AF/01/76 = 175/01/118 |  | Actual values parameters | R/WS | INT (Signed32) | - |  | - | [Total Quantity] (FS1C) | [Application Parameters] (APr-) | 789
FS1J | Lowest Flow | 16#3EB8 = 16056 | 16#2082/39 | 16#B1/01/39 = 177/01/57 | - | Configuration and settings | R | INT (Signed16) | (call FlowRateUnitSelection [SUFR]) |  | (call FlowRateUnitSelection [SUFR]) ... (call FlowRateUnitSelection [SUFR]) | [Lowest Flow] (FS1J) | [Application Parameters] (APr-) | 790
FS1K | Highest Flow | 16#3EB7 = 16055 | 16#2082/38 | 16#B1/01/38 = 177/01/56 | - | Configuration and settings | R | INT (Signed16) | (call FlowRateUnitSelection [SUFR]) |  | (call FlowRateUnitSelection [SUFR]) ... (call FlowRateUnitSelection [SUFR]) | [Highest Flow] (FS1 ) | [Application Parameters] (APr-) | 791
FS1V | Installation Flow | 16#3D63 = 15715 | 16#207F/10 | 16#AF/01/74 = 175/01/116 | - | Actual values parameters | R | INT (Signed16) | (call FlowRateUnitSelection [SUFR]) |  | (call FlowRateUnitSelection [SUFR]) ... (call FlowRateUnitSelection [SUFR]) | [Installation Flow] (FS1U) | [Display] (SUP-) | 792
FSPD | Fan Speed | 16#0CBF = 3263 | 16#2002/40 | 16#71/01/40 = 113/01/64 | - | Measurement parameters | R | UINT (Unsigned16) | 1 rpm |  | 0 rpm ... 65535 rpm |  |  | 793
FTDL | Low Freq.Threshold | 16#2B03 = 11011 | 16#2050/C | 16#98/01/0C = 152/01/12 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 500.0 Hz | [Low Freq.Threshold] (FtdL) | [Threshold reached] (tHrE-) [Settings] (SEt-) | 794
FTO | Overload T.B.Rest. | 16#3857 = 14423 | 16#2072/18 | 16#A9/01/18 = 169/01/24 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 min | 0 min | 0 min ... 6 min | [Overload T.B.Rest.] (FtO) | [Process overload] (OLd-) [Settings] (SEt-) | 795
FTU | Underload T.B.Rest. | 16#384D = 14413 | 16#2072/E | 16#A9/01/0E = 169/01/14 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 min | 0 min | 0 min ... 6 min | [Underload T.B.Rest.] (FtU) | [Process underload] (ULd-) [Settings] (SEt-) | 796
GRFL | Ground Fault Activation | 16#1B76 = 7030 | 16#2028/1F | 16#84/01/1F = 132/01/31 | - | Configuration and settings | R/WS | INT (Signed16) | 0.1 % | [Yes] (YES) | [No] (InH) ... 100.0 % | [Ground Fault Activation] (GrFL) | [Ground Fault] (GrFL-) | 797
HEG | Head Dynamic Gain | 16#3E83 = 16003 | 16#2082/4 | 16#B1/01/04 = 177/01/04 | - | Configuration and settings | R/W | INT (Signed16) | 0.1 % | 0.0 % | 0.0 % ... 100.0 % | [Head Dynamic Gain] (HEG) | [Flow estimation] (SFE-) | 798
HEO | Head Static Offset | 16#3E84 = 16004 | 16#2082/5 | 16#B1/01/05 = 177/01/05 | - | Configuration and settings | R/W | INT (Signed16) | 0.1 % | 0.0 % | -100.0 % ... 100.0 % | [Head Static Offset] (HEO) | [Flow estimation] (SFE-) | 799
HFPB | HighFlowError Resp | 16#3DF7 = 15863 | 16#2080/40 | 16#B0/01/40 = 176/01/64 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ramp stop] (rMP) | - | [HighFlowError Resp] (HFPb) | [High flow monitoring] (HFP-) | 800
HFPD | HighFlowError Delay | 16#3DF6 = 15862 | 16#2080/3F | 16#B0/01/3F = 176/01/63 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | 10 s | 0 s ... 3600 s | [HighFlowError Delay] (HFPd) | [Settings] (SEt-) [High flow monitoring] (HFP-) | 801
HFPL | HighFlow MaxLevel | 16#3DF5 = 15861 | 16#2080/3E | 16#B0/01/3E = 176/01/62 | - | Configuration and settings | R/W | INT (Signed16) | (call FlowRateUnitSelection [SUFR]) | (call FlowRateUnitSelection [SUFR]) | (call FlowRateUnitSelection [SUFR]) ... (call FlowRateUnitSelection [SUFR]) | [HighFlow MaxLevel] (HFPL) | [Settings] (SEt-) [High flow monitoring] (HFP-) | 802
HFPM | HighFlow activation | 16#3DF4 = 15860 | 16#2080/3D | 16#B0/01/3D = 176/01/61 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [HighFlow activation] (HFPM) | [High flow monitoring] (HFP-) | 803
HS9 | Drive state | 16#1CA1 = 7329 | 16#202B/1E | 16#85/01/82 = 133/01/130 | HMIS | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 804
HSA | Drive state | 16#1E28 = 7720 | 16#202F/15 | 16#87/01/79 = 135/01/121 | HMIS | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 805
HSB | Drive state | 16#1E29 = 7721 | 16#202F/16 | 16#87/01/7A = 135/01/122 | HMIS | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 806
HSC | Drive state | 16#1E2A = 7722 | 16#202F/17 | 16#87/01/7B = 135/01/123 | HMIS | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 807
HSD | Drive state | 16#1E2B = 7723 | 16#202F/18 | 16#87/01/7C = 135/01/124 | HMIS | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 808
HSE | Drive state | 16#1E2C = 7724 | 16#202F/19 | 16#87/01/7D = 135/01/125 | HMIS | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 809
HSF | Drive state | 16#1E2D = 7725 | 16#202F/1A | 16#87/01/7E = 135/01/126 | HMIS | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 810
IC0 | Input Energy (Wh) | 16#2982 = 10626 | 16#204C/1B | 16#96/01/1B = 150/01/27 | - | Actual values parameters | R/WS | UINT (Unsigned16) | 1 Wh |  | 0 Wh ... 999 Wh |  |  | 811
IC1 | Input Energy (kWh) | 16#2983 = 10627 | 16#204C/1C | 16#96/01/1C = 150/01/28 | - | Actual values parameters | R/WS | UINT (Unsigned16) | 1 kWh |  | 0 kWh ... 999 kWh |  |  | 812
IC2 | Input Energy (MWh) | 16#2984 = 10628 | 16#204C/1D | 16#96/01/1D = 150/01/29 | - | Actual values parameters | R/WS | UINT (Unsigned16) | 1 MWh |  | 0 MWh ... 999 MWh |  |  | 813
IC3 | Input Energy (GWh) | 16#2985 = 10629 | 16#204C/1E | 16#96/01/1E = 150/01/30 | - | Actual values parameters | R/WS | UINT (Unsigned16) | 1 GWh |  | 0 GWh ... 999 GWh |  |  | 814
IC4 | Input Energy (TWh) | 16#2986 = 10630 | 16#204C/1F | 16#96/01/1F = 150/01/31 | - | Actual values parameters | R/WS | UINT (Unsigned16) | 1 TWh |  | 0 TWh ... 999 TWh |  |  | 815
IDLM | Energy Saving Delay | 16#3625 = 13861 | 16#206C/3E | 16#A6/01/3E = 166/01/62 | - | Configuration and settings | R/WS | INT (Signed16) | 1 s | Refer to programming manual | [No] (nO) ... 32400 s | [Energy Saving Delay] (IdLM) | [Stop and Go] (StG-) | 816
IDLS | Energy Saving Assign | 16#3624 = 13860 | 16#206C/3D | 16#A6/01/3D = 166/01/61 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Assigned] (nO) | - | [Energy Saving Assign] (IdLS) | [Stop and Go] (StG-) | 817
IE0 | Real Input Energy (Wh) | 16#298C = 10636 | 16#204C/25 | 16#96/01/25 = 150/01/37 | - | Actual values parameters | R/WS | INT (Signed16) | 1 Wh |  | -999 Wh ... 999 Wh | [Real Input Energy (Wh)] (IE0) | [Elec Ener Input Counter] (ELI-) | 818
IE1 | Real Input Energy (kWh) | 16#298D = 10637 | 16#204C/26 | 16#96/01/26 = 150/01/38 | - | Actual values parameters | R/WS | INT (Signed16) | 1 kWh |  | -999 kWh ... 999 kWh | [Real Input Energy (kWh)] (IE1) | [Elec Ener Input Counter] (ELI-) | 819
IE2 | Real Input Energy(MWh) | 16#298E = 10638 | 16#204C/27 | 16#96/01/27 = 150/01/39 | - | Actual values parameters | R/WS | INT (Signed16) | 1 MWh |  | -999 MWh ... 999 MWh | [Real Input Energy(MWh)] (IE2) | [Elec Ener Input Counter] (ELI-) | 820
IE3 | Real Input Energy(GWh) | 16#298F = 10639 | 16#204C/28 | 16#96/01/28 = 150/01/40 | - | Actual values parameters | R/WS | INT (Signed16) | 1 GWh |  | -999 GWh ... 999 GWh | [Real Input Energy(GWh)] (IE3) | [Elec Ener Input Counter] (ELI-) | 821
IE4 | Real Input Energy(TWh) | 16#2990 = 10640 | 16#204C/29 | 16#96/01/29 = 150/01/41 | - | Actual values parameters | R/WS | INT (Signed16) | 1 TWh |  | -999 TWh ... 999 TWh | [Real Input Energy(TWh)] (IE4) | [Elec Ener Input Counter] (ELI-) | 822
IL1I |  | 16#1451 = 5201 | 16#2016/2 | 16#7B/01/02 = 123/01/02 | IL1I | I/O parameters | R | WORD (BitString16) | - |  | - |  |  | 823
INRC |  | 16#2649 = 9801 | 16#2044/2 | 16#92/01/02 = 146/01/02 | CINR | Configuration and settings | R | WORD (Enumeration) | - |  | - |  |  | 824
INRL |  | 16#264C = 9804 | 16#2044/5 | 16#92/01/05 = 146/01/05 | CINR | Configuration and settings | R | WORD (Enumeration) | - |  | - |  |  | 825
INRP |  | 16#264A = 9802 | 16#2044/3 | 16#92/01/03 = 146/01/03 | CINR | Configuration and settings | R | WORD (Enumeration) | - |  | - |  |  | 826
INRR |  | 16#264B = 9803 | 16#2044/4 | 16#92/01/04 = 146/01/04 | CINR | Configuration and settings | R | WORD (Enumeration) | - |  | - |  |  | 827
INRT |  | 16#264D = 9805 | 16#2044/6 | 16#92/01/06 = 146/01/06 | CINR | Configuration and settings | R | WORD (Enumeration) | - |  | - |  |  | 828
INTI |  | 16#264E = 9806 | 16#2044/7 | 16#92/01/07 = 146/01/07 | CINR | Configuration and settings | R | WORD (Enumeration) | - |  | - |  |  | 829
IP9 | ETI state word | 16#1C3D = 7229 | 16#202A/1E | 16#85/01/1E = 133/01/30 | IP9 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 830
IPA | ETI state word | 16#1DC4 = 7620 | 16#202E/15 | 16#87/01/15 = 135/01/21 | IPA | History parameters | R | WORD (BitString16) | - |  | - |  |  | 831
IPAD | iPar Error Code | 16#FB18 = 64280 |  | = | - | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 5 | [iPar Error Code] (IPAd) | [PROFINET DIAG] (Prn-) | 832
IPB | ETI state word | 16#1DC5 = 7621 | 16#202E/16 | 16#87/01/16 = 135/01/22 | IPB | History parameters | R | WORD (BitString16) | - |  | - |  |  | 833
IPC | ETI state word | 16#1DC6 = 7622 | 16#202E/17 | 16#87/01/17 = 135/01/23 | IPC | History parameters | R | WORD (BitString16) | - |  | - |  |  | 834
IPD | ETI state word | 16#1DC7 = 7623 | 16#202E/18 | 16#87/01/18 = 135/01/24 | IPD | History parameters | R | WORD (BitString16) | - |  | - |  |  | 835
IPE | ETI state word | 16#1DC8 = 7624 | 16#202E/19 | 16#87/01/19 = 135/01/25 | IPE | History parameters | R | WORD (BitString16) | - |  | - |  |  | 836
IPF | ETI state word | 16#1DC9 = 7625 | 16#202E/1A | 16#87/01/1A = 135/01/26 | IPF | History parameters | R | WORD (BitString16) | - |  | - |  |  | 837
IPPB | InletPresError Resp | 16#3E2A = 15914 | 16#2081/F | 16#B0/01/73 = 176/01/115 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ramp stop] (rMP) | - | [InletPresError Resp] (IPPb) | [Inlet pressure monitoring] (IPP-) | 838
IPPC | InletPres Max Comp | 16#3E29 = 15913 | 16#2081/E | 16#B0/01/72 = 176/01/114 | - | Configuration and settings | R/W | INT (Signed16) | (call PressureUnitSelected [SUPR]) | (call PressureUnitSelected [SUPR]) | (call PressureUnitSelected [SUPR]) ... (call PressureUnitSelected [SUPR]) | [InletPres Max Comp] (IPPC) | [Settings] (SEt-) [Inlet pressure monitoring] (IPP-) | 839
IPPH | InletPres High Thd | 16#3E27 = 15911 | 16#2081/C | 16#B0/01/70 = 176/01/112 | - | Configuration and settings | R/W | INT (Signed16) | (call PressureUnitSelected [SUPR]) | (call PressureUnitSelected [SUPR]) | (call PressureUnitSelected [SUPR]) ... (call PressureUnitSelected [SUPR]) | [InletPres High Thd] (IPPH) | [Settings] (SEt-) [Inlet pressure monitoring] (IPP-) | 840
IPPL | InletPres Low Thd | 16#3E28 = 15912 | 16#2081/D | 16#B0/01/71 = 176/01/113 | - | Configuration and settings | R/W | INT (Signed16) | (call PressureUnitSelected [SUPR]) | (call PressureUnitSelected [SUPR]) | (call PressureUnitSelected [SUPR]) ... (call PressureUnitSelected [SUPR]) | [InletPres Low Thd] (IPPL) | [Settings] (SEt-) [Inlet pressure monitoring] (IPP-) | 841
IPPM | InletPres Monitoring | 16#3E26 = 15910 | 16#2081/B | 16#B0/01/6F = 176/01/111 | IPPM | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [InletPres Monitoring] (IPPM) | [Inlet pressure monitoring] (IPP-) | 842
IPR |  | 16#0C92 = 3218 | 16#2002/13 | 16#71/01/13 = 113/01/19 | - | Actual values parameters | R | INT (Signed16) | 1 % |  | (---) | (IPr) | [Elec Ener Input Counter] (ELI-) | 843
IPRW | Active Input Power | 16#0CDE = 3294 | 16#2002/5F | 16#71/01/5F = 113/01/95 | - | Actual values parameters | R | INT (Signed16) | Refer to programming manual |  | Depends of rating | [Active Input Power] (IPrW) | [Elec Ener Input Counter] (ELI-) | 844
JACC | Anti-Jam Fwd Acc | 16#3E37 = 15927 | 16#2081/1C | 16#B0/01/80 = 176/01/128 | - | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | Refer to programming manual | [Anti-Jam Fwd Acc] (JACC) | [Settings] (SEt-) [Anti-Jam Monit] (JAM-) | 845
JACR | Anti-Jam Rv Acc | 16#3E38 = 15928 | 16#2081/1D | 16#B0/01/81 = 176/01/129 | - | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | Refer to programming manual | [Anti-Jam Rv Acc] (JACr) | [Settings] (SEt-) [Anti-Jam Monit] (JAM-) | 846
JAMB | Anti-Jam Error Resp | 16#3E42 = 15938 | 16#2081/27 | 16#B0/01/8B = 176/01/139 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel Stop] (YES) | - | [Anti-Jam Error Resp] (JAMb) | [Anti-Jam Monit] (JAM-) | 847
JAMN | Anti-Jam Max Seq | 16#3E40 = 15936 | 16#2081/25 | 16#B0/01/89 = 176/01/137 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 2 | 1 ... 99 | [Anti-Jam Max Seq] (JAMn) | [Settings] (SEt-) [Anti-Jam Monit] (JAM-) | 848
JAMT | Anti-Jam Interval | 16#3E41 = 15937 | 16#2081/26 | 16#B0/01/8A = 176/01/138 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | 60 s | 0 s ... 3600 s | [Anti-Jam Interval] (JAMt) | [Settings] (SEt-) [Anti-Jam Monit] (JAM-) | 849
JATC | Anti-Jam Auto Trig | 16#3E31 = 15921 | 16#2081/16 | 16#B0/01/7A = 176/01/122 | JATC | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Anti-Jam Auto Trig] (JAtC) | [Anti-Jam Monit] (JAM-) | 850
JDEC | Anti-Jam Fwd Dec | 16#3E35 = 15925 | 16#2081/1A | 16#B0/01/7E = 176/01/126 | - | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | Refer to programming manual | [Anti-Jam Fwd Dec] (JdEC) | [Settings] (SEt-) [Anti-Jam Monit] (JAM-) | 851
JDER | Anti-Jam Rv Dec | 16#3E36 = 15926 | 16#2081/1B | 16#B0/01/7F = 176/01/127 | - | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | Refer to programming manual | [Anti-Jam Rv Dec] (JdEr) | [Settings] (SEt-) [Anti-Jam Monit] (JAM-) | 852
JETC | Anti-Jam Ext Trig | 16#3E30 = 15920 | 16#2081/15 | 16#B0/01/79 = 176/01/121 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Assigned] (nO) | - | [Anti-Jam Ext Trig] (JEtC) | [Anti-Jam Monit] (JAM-) | 853
JFDS | Anti-Jam Fwd Speed | 16#3E3B = 15931 | 16#2081/20 | 16#B0/01/84 = 176/01/132 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [Anti-Jam Fwd Speed] (JFdS) | [Settings] (SEt-) [Anti-Jam Monit] (JAM-) | 854
JFDT | Anti-Jam Fwd Time | 16#3E39 = 15929 | 16#2081/1E | 16#B0/01/82 = 176/01/130 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | 1 s | 0 s ... 300 s | [Anti-Jam Fwd Time] (JFdt) | [Settings] (SEt-) [Anti-Jam Monit] (JAM-) | 855
JNBC | Anti-Jam Cycle Nb | 16#3E3E = 15934 | 16#2081/23 | 16#B0/01/87 = 176/01/135 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 10 | 1 ... 100 | [Anti-Jam Cycle Nb] (JnbC) | [Settings] (SEt-) [Anti-Jam Monit] (JAM-) | 856
JP | Jockey Selection | 16#3DD6 = 15830 | 16#2080/1F | 16#B0/01/1F = 176/01/31 | CSLOUT | Configuration and settings | R/WS | WORD (Enumeration) | - |  | - | [Jockey Selection] (JP) | [Jump frequency] (JUF-) [Settings] (SEt-) | 857
JPRD | Delay to start | 16#3DD8 = 15832 | 16#2080/21 | 16#B0/01/21 = 176/01/33 | - | Configuration and settings | R/W | INT (Signed16) | 1 s | 0 s | 0 s ... 3600 s | [Delay to start] (JPrd) | [Settings] (SEt-) [Jockey pump] (J P-) | 858
JPRP | Minimum Pressure | 16#3DD7 = 15831 | 16#2080/20 | 16#B0/01/20 = 176/01/32 | - | Configuration and settings | R/W | INT (Signed16) | (call PressureUnitSelected [SUPR]) | (call PressureUnitSelected [SUPR]) | (call PressureUnitSelected [SUPR]) ... (call PressureUnitSelected [SUPR]) | [Minimum Pressure] (JPrP) | [Settings] (SEt-) [Jockey pump] (J P-) | 859
JPRS | Reference Speed | 16#3DDA = 15834 | 16#2080/23 | 16#B0/01/23 = 176/01/35 | - | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | HSP | 0.0 Hz ... 599.0 Hz | [Reference Speed] (JPrS) | [Settings] (SEt-) [Jockey pump] (J P-) | 860
JPSP | Maximum Pressure | 16#3DD9 = 15833 | 16#2080/22 | 16#B0/01/22 = 176/01/34 | - | Configuration and settings | R/W | INT (Signed16) | (call PressureUnitSelected [SUPR]) | (call PressureUnitSelected [SUPR]) | (call PressureUnitSelected [SUPR]) ... (call PressureUnitSelected [SUPR]) | [Maximum Pressure] (JPSP) | [Settings] (SEt-) [Jockey pump] (J P-) | 861
JPWD | Wake up Delay | 16#3DDB = 15835 | 16#2080/24 | 16#B0/01/24 = 176/01/36 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | [No] (nO) | [No] (nO) ... 3600 s | [Wake up Delay] (JPWd) | [Settings] (SEt-) [Jockey pump] (J P-) | 862
JRVS | Anti-Jam Rv Speed | 16#3E3C = 15932 | 16#2081/21 | 16#B0/01/85 = 176/01/133 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [Anti-Jam Rv Speed] (JrUS) | [Settings] (SEt-) [Anti-Jam Monit] (JAM-) | 863
JRVT | Anti-Jam Rv Time | 16#3E3A = 15930 | 16#2081/1F | 16#B0/01/83 = 176/01/131 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | 1 s | 0 s ... 300 s | [Anti-Jam Rv Time] (JrUt) | [Settings] (SEt-) [Anti-Jam Monit] (JAM-) | 864
JTCD | Anti-Jam Start Delay | 16#3E34 = 15924 | 16#2081/19 | 16#B0/01/7D = 176/01/125 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | 10 s | 0 s ... 3600 s | [Anti-Jam Start Delay] (JtCd) | [Settings] (SEt-) [Anti-Jam Monit] (JAM-) | 865
JTCL | Anti-Jam Torque | 16#3E33 = 15923 | 16#2081/18 | 16#B0/01/7C = 176/01/124 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 % | 110.0 % | 10.0 % ... 150.0 % | [Anti-Jam Torque] (JtCL) | [Settings] (SEt-) [Anti-Jam Monit] (JAM-) | 866
JTCT | Anti-Jam Trigger Time | 16#3E32 = 15922 | 16#2081/17 | 16#B0/01/7B = 176/01/123 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 h | 24 h | 0 h ... 9999 h | [Anti-Jam Trigger Time] (JtCt) | [Settings] (SEt-) [Anti-Jam Monit] (JAM-) | 867
JZST | Anti-Jam Stop Time | 16#3E3D = 15933 | 16#2081/22 | 16#B0/01/86 = 176/01/134 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | 0 s | 0 s ... 300 s | [Anti-Jam Stop Time] (JZSt) | [Settings] (SEt-) [Anti-Jam Monit] (JAM-) | 868
L11D | DI11 Delay | 16#0FAB = 4011 | 16#200A/C | 16#75/01/0C = 117/01/12 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 5 ms | 0 ms ... 200 ms | [DI11 Delay] (L11d) | [DI11 Configuration] (dI11-) | 869
L12D | DI12 Delay | 16#0FAC = 4012 | 16#200A/D | 16#75/01/0D = 117/01/13 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 5 ms | 0 ms ... 200 ms | [DI12 Delay] (L12d) | [DI12 Configuration] (dI12-) | 870
L13D | DI13 Delay | 16#0FAD = 4013 | 16#200A/E | 16#75/01/0E = 117/01/14 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 5 ms | 0 ms ... 200 ms | [DI13 Delay] (L13d) | [DI13 Configuration] (dI13-) | 871
L14D | DI14 Delay | 16#0FAE = 4014 | 16#200A/F | 16#75/01/0F = 117/01/15 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 5 ms | 0 ms ... 200 ms | [DI14 Delay] (L14d) | [DI14 Configuration] (dI14-) | 872
L15D | DI15 Delay | 16#0FAF = 4015 | 16#200A/10 | 16#75/01/10 = 117/01/16 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 5 ms | 0 ms ... 200 ms | [DI15 Delay] (L15d) | [DI15 Configuration] (dI15-) | 873
L16D | DI16 Delay | 16#0FB0 = 4016 | 16#200A/11 | 16#75/01/11 = 117/01/17 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 5 ms | 0 ms ... 200 ms | [DI16 Delay] (L16d) | [DI16 Configuration] (dI16-) | 874
LALR | Last Warning | 16#325A = 12890 | 16#2062/5B | 16#A1/01/5B = 161/01/91 | ALR | Actual values parameters | R | WORD (Enumeration) | - |  | - | [Last Warning] (LALr) | [Diag. data] (ddt-) | 875
LCAC | LifeCycle Warning | 16#3598 = 13720 | 16#206B/15 | 16#A5/01/79 = 165/01/121 | N_Y | Configuration and settings | R/W | WORD (Enumeration) | - | [Yes] (YES) | - | [LifeCycle Warning] (LCAC) | [Drive warranty mgnt] (dWMA-) | 876
LCAD | Warranty expired | 16#3599 = 13721 | 16#206B/16 | 16#A5/01/7A = 165/01/122 | - | Actual values parameters | R | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Warranty expired] (LCAd) | [Drive warranty mgnt] (dWMA-) | 877
LCP9 | Motor current | 16#1C51 = 7249 | 16#202A/32 | 16#85/01/32 = 133/01/50 | - | History parameters | R | INT (Signed16) | Refer to programming manual |  | Depends of rating |  |  | 878
LCPA | Motor current | 16#1DD8 = 7640 | 16#202E/29 | 16#87/01/29 = 135/01/41 | - | History parameters | R | INT (Signed16) | Refer to programming manual |  | Depends of rating |  |  | 879
LCPB | Motor current | 16#1DD9 = 7641 | 16#202E/2A | 16#87/01/2A = 135/01/42 | - | History parameters | R | INT (Signed16) | Refer to programming manual |  | Depends of rating |  |  | 880
LCPC | Motor current | 16#1DDA = 7642 | 16#202E/2B | 16#87/01/2B = 135/01/43 | - | History parameters | R | INT (Signed16) | Refer to programming manual |  | Depends of rating |  |  | 881
LCPD | Motor current | 16#1DDB = 7643 | 16#202E/2C | 16#87/01/2C = 135/01/44 | - | History parameters | R | INT (Signed16) | Refer to programming manual |  | Depends of rating |  |  | 882
LCPE | Motor current | 16#1DDC = 7644 | 16#202E/2D | 16#87/01/2D = 135/01/45 | - | History parameters | R | INT (Signed16) | Refer to programming manual |  | Depends of rating |  |  | 883
LCPF | Motor current | 16#1DDD = 7645 | 16#202E/2E | 16#87/01/2E = 135/01/46 | - | History parameters | R | INT (Signed16) | Refer to programming manual |  | Depends of rating |  |  | 884
LDD1 | Log Distrib. Data 1 | 16#4010 = 16400 | 16#2086/1 | 16#B3/01/01 = 179/01/01 | LDD | Configuration and settings | R/W | WORD (Enumeration) | - | [Distrib. Log. DISABLE] (nO) | - | [Log Distrib. Data 1] (Ldd1) | [Log dstrb prm select] (LdP-) | 885
LDD2 | Log Distrib.Data 2 | 16#4012 = 16402 | 16#2086/3 | 16#B3/01/03 = 179/01/03 | LDD | Configuration and settings | R/W | WORD (Enumeration) | - | [Distrib. Log. DISABLE] (nO) | - | [Log Distrib.Data 2] (Ldd2) | [Log dstrb prm select] (LdP-) | 886
LDD3 | Log Distrib. Data 3 | 16#4014 = 16404 | 16#2086/5 | 16#B3/01/05 = 179/01/05 | LDD | Configuration and settings | R/W | WORD (Enumeration) | - | [Distrib. Log. DISABLE] (nO) | - | [Log Distrib. Data 3] (Ldd3) | [Log dstrb prm select] (LdP-) | 887
LDD4 | Log Distrib. Data 4 | 16#4016 = 16406 | 16#2086/7 | 16#B3/01/07 = 179/01/07 | LDD | Configuration and settings | R/W | WORD (Enumeration) | - | [Distrib. Log. DISABLE] (nO) | - | [Log Distrib. Data 4] (Ldd4) | [Log dstrb prm select] (LdP-) | 888
LDEN | Log Distrib State | 16#4019 = 16409 | 16#2086/A | 16#B3/01/0A = 179/01/10 | LDEN | Configuration and settings | R/W | WORD (Enumeration) | - | [Stop] (StOP) | - | [Log Distrib State] (LdEn) | [Distributed logging] (dLO-) | 889
LDM1 | Dist Max Val 1 | 16#4011 = 16401 | 16#2086/2 | 16#B3/01/02 = 179/01/02 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 | (call LDM_DefaultValue [LDD1]) | 10 ... 65535 | [Dist Max Val 1] (LdM1) | [Distributed logging] (dLO-) | 890
LDM2 | Dist Max Val 2 | 16#4013 = 16403 | 16#2086/4 | 16#B3/01/04 = 179/01/04 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 | (call LDM_DefaultValue [LDD2]) | 10 ... 65535 | [Dist Max Val 2] (LdM2) | [Distributed logging] (dLO-) | 891
LDM3 | Dist Max Val 3 | 16#4015 = 16405 | 16#2086/6 | 16#B3/01/06 = 179/01/06 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 | (call LDM_DefaultValue [LDD3]) | 10 ... 65535 | [Dist Max Val 3] (LdM3) | [Distributed logging] (dLO-) | 892
LDM4 | Dist Max Val 4 | 16#4017 = 16407 | 16#2086/8 | 16#B3/01/08 = 179/01/08 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 | (call LDM_DefaultValue [LDD4]) | 10 ... 65535 | [Dist Max Val 4] (LdM4) | [Distributed logging] (dLO-) | 893
LDST | Log Distrib Spl Time | 16#4018 = 16408 | 16#2086/9 | 16#B3/01/09 = 179/01/09 | LDST | Configuration and settings | R/W | WORD (Enumeration) | - | [1 second] (1S) | - | [Log Distrib Spl Time] (LdSt) | [Distributed logging] (dLO-) | 894
LFL1 | AI1 4-20mA loss | 16#1B69 = 7017 | 16#2028/12 | 16#84/01/12 = 132/01/18 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ignore] (nO) | - | [AI1 4-20mA loss] (LFL1) | [4-20 mA loss] (LFL-) | 895
LFL2 | AI2 4-20mA loss | 16#1B5B = 7003 | 16#2028/4 | 16#84/01/04 = 132/01/04 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ignore] (nO) | - | [AI2 4-20mA loss] (LFL2) | [4-20 mA loss] (LFL-) | 896
LFL4 | AI4 4-20mA loss | 16#1B66 = 7014 | 16#2028/F | 16#84/01/0F = 132/01/15 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ignore] (nO) | - | [AI4 4-20mA loss] (LFL4) | [4-20 mA loss] (LFL-) | 897
LFL5 | AI5 4-20mA loss | 16#1B6B = 7019 | 16#2028/14 | 16#84/01/14 = 132/01/20 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ignore] (nO) | - | [AI5 4-20mA loss] (LFL5) | [4-20 mA loss] (LFL-) | 898
LOC | Ovld Detection Thr. | 16#3859 = 14425 | 16#2072/1A | 16#A9/01/1A = 169/01/26 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 110 % | 70 % ... 150 % | [Ovld Detection Thr.] (LOC) | [Process overload] (OLd-) [Settings] (SEt-) | 899
MD0 |  | 16#1C84 = 7300 | 16#202B/1 | 16#85/01/65 = 133/01/101 | - | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 900
MD1 |  | 16#1C85 = 7301 | 16#202B/2 | 16#85/01/66 = 133/01/102 | - | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 901
MD2 |  | 16#1C86 = 7302 | 16#202B/3 | 16#85/01/67 = 133/01/103 | - | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 902
MD3 |  | 16#1C87 = 7303 | 16#202B/4 | 16#85/01/68 = 133/01/104 | - | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 903
MD4 |  | 16#1C88 = 7304 | 16#202B/5 | 16#85/01/69 = 133/01/105 | - | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 904
MD5 |  | 16#1C89 = 7305 | 16#202B/6 | 16#85/01/6A = 133/01/106 | - | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 905
MD6 |  | 16#1C8A = 7306 | 16#202B/7 | 16#85/01/6B = 133/01/107 | - | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 906
MD7 |  | 16#1C8B = 7307 | 16#202B/8 | 16#85/01/6C = 133/01/108 | - | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 907
MD8 |  | 16#1C8C = 7308 | 16#202B/9 | 16#85/01/6D = 133/01/109 | - | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 908
MD9 |  | 16#1C8D = 7309 | 16#202B/A | 16#85/01/6E = 133/01/110 | - | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 909
MDA |  | 16#1E14 = 7700 | 16#202F/1 | 16#87/01/65 = 135/01/101 | - | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 910
MDB |  | 16#1E15 = 7701 | 16#202F/2 | 16#87/01/66 = 135/01/102 | - | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 911
MDC |  | 16#1E16 = 7702 | 16#202F/3 | 16#87/01/67 = 135/01/103 | - | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 912
MDD |  | 16#1E17 = 7703 | 16#202F/4 | 16#87/01/68 = 135/01/104 | - | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 913
MDE |  | 16#1E18 = 7704 | 16#202F/5 | 16#87/01/69 = 135/01/105 | - | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 914
MDF |  | 16#1E19 = 7705 | 16#202F/6 | 16#87/01/6A = 135/01/106 | - | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 915
ME0 | Motor Consumption(Wh) | 16#2969 = 10601 | 16#204C/2 | 16#96/01/02 = 150/01/02 | - | Actual values parameters | R/WS | UINT (Unsigned16) | 1 Wh |  | 0 Wh ... 999 Wh | [Motor Consumption(Wh)] (ME0) | [Mechanical Energy] (MEC-) | 916
ME1 | Motor Consumption(kWh) | 16#296A = 10602 | 16#204C/3 | 16#96/01/03 = 150/01/03 | - | Actual values parameters | R/WS | UINT (Unsigned16) | 1 kWh |  | 0 kWh ... 999 kWh | [Motor Consumption(kWh)] (ME1) | [Mechanical Energy] (MEC-) | 917
ME2 | Motor Consumption(MWh) | 16#296B = 10603 | 16#204C/4 | 16#96/01/04 = 150/01/04 | - | Actual values parameters | R/WS | UINT (Unsigned16) | 1 MWh |  | 0 MWh ... 999 MWh | [Motor Consumption(MWh)] (ME2) | [Mechanical Energy] (MEC-) | 918
ME3 | Motor Consumption(GWh) | 16#296C = 10604 | 16#204C/5 | 16#96/01/05 = 150/01/05 | - | Actual values parameters | R/WS | UINT (Unsigned16) | 1 GWh |  | 0 GWh ... 999 GWh | [Motor Consumption(GWh)] (ME3) | [Mechanical Energy] (MEC-) | 919
ME4 | Motor Consumption(TWh) | 16#296D = 10605 | 16#204C/6 | 16#96/01/06 = 150/01/06 | - | Actual values parameters | R/WS | UINT (Unsigned16) | 1 TWh |  | 0 TWh ... 999 TWh | [Motor Consumption(TWh)] (ME4) | [Mechanical Energy] (MEC-) | 920
MOEP | Peak Output Power | 16#2991 = 10641 | 16#204C/2A | 16#96/01/2A = 150/01/42 | - | Status parameters | R | UINT (Unsigned16) | Refer to programming manual |  | Depends of rating | [Peak Output Power] (MOEP) | [Elec Ener Output Counter] (ELO-) | 921
NFHP | High Power | 16#3E5B = 15963 | 16#2081/40 | 16#B0/01/A4 = 176/01/164 | - | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | Depends of rating | Depends of rating | [High Power] (nFHP) | [Dry run Monit] (dYr-) | 922
NFHS | High Speed | 16#3E5A = 15962 | 16#2081/3F | 16#B0/01/A3 = 176/01/163 | - | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [High Speed] (nFHS) | [Dry run Monit] (dYr-) | 923
NFLP | Low Power | 16#3E59 = 15961 | 16#2081/3E | 16#B0/01/A2 = 176/01/162 | - | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | Depends of rating | Depends of rating | [Low Power] (nFLP) | [Dry run Monit] (dYr-) | 924
NFLS | Low Speed | 16#3E58 = 15960 | 16#2081/3D | 16#B0/01/A1 = 176/01/161 | - | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [Low Speed] (nFLS) | [Dry run Monit] (dYr-) | 925
NSM | Nb Of Starts | 16#0CBC = 3260 | 16#2002/3D | 16#71/01/3D = 113/01/61 |  | Configuration and settings | R/WS | UINT (Unsigned32) | - |  | - | [Nb Of Starts] (nSM) | [Diag. data] (ddt-) | 926
OC0 | Elc Energy Cons | 16#296E = 10606 | 16#204C/7 | 16#96/01/07 = 150/01/07 | - | Actual values parameters | R/WS | UINT (Unsigned16) | 1 Wh |  | 0 Wh ... 999 Wh | [Elc Energy Cons] (OC0) | [kWh Counters] ( WC-) | 927
OC1 | Elc Energy Cons | 16#296F = 10607 | 16#204C/8 | 16#96/01/08 = 150/01/08 | - | Actual values parameters | R/WS | UINT (Unsigned16) | 1 kWh |  | 0 kWh ... 999 kWh | [Elc Energy Cons] (OC1) | [kWh Counters] ( WC-) | 928
OC2 | Elc Energy Cons | 16#2970 = 10608 | 16#204C/9 | 16#96/01/09 = 150/01/09 | - | Actual values parameters | R/WS | UINT (Unsigned16) | 1 MWh |  | 0 MWh ... 999 MWh | [Elc Energy Cons] (OC2) | [kWh Counters] ( WC-) | 929
OC3 | Elc Energy Cons | 16#2971 = 10609 | 16#204C/A | 16#96/01/0A = 150/01/10 | - | Actual values parameters | R/WS | UINT (Unsigned16) | 1 GWh |  | 0 GWh ... 999 GWh | [Elc Energy Cons] (OC3) | [kWh Counters] ( WC-) | 930
OC4 | Elc Energy Cons | 16#2972 = 10610 | 16#204C/B | 16#96/01/0B = 150/01/11 | - | Actual values parameters | R/WS | UINT (Unsigned16) | 1 TWh |  | 0 TWh ... 999 TWh | [Elc Energy Cons] (OC4) | [kWh Counters] ( WC-) | 931
OCA7 | Scan.Out7 address | 16#3C43 = 15427 | 16#207C/1C | 16#AE/01/1C = 174/01/28 | - | Communication parameters | [always] | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 932
OCA8 | Scan.Out8 address | 16#3C44 = 15428 | 16#207C/1D | 16#AE/01/1D = 174/01/29 | - | Communication parameters | [always] | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 933
OCA9 | Scan.Out9 address | 16#3C45 = 15429 | 16#207C/1E | 16#AE/01/1E = 174/01/30 | - | Communication parameters | [always] | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 934
OCAA | Scan.Out10 address | 16#3C46 = 15430 | 16#207C/1F | 16#AE/01/1F = 174/01/31 | - | Communication parameters | [always] | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 935
OCAB | Scan.Out11 address | 16#3C47 = 15431 | 16#207C/20 | 16#AE/01/20 = 174/01/32 | - | Communication parameters | [always] | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 936
OCAC | Scan.Out12 address | 16#3C48 = 15432 | 16#207C/21 | 16#AE/01/21 = 174/01/33 | - | Communication parameters | [always] | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 937
OCAD | Scan.Out13 address | 16#3C49 = 15433 | 16#207C/22 | 16#AE/01/22 = 174/01/34 | - | Communication parameters | [always] | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 938
OCAE | Scan.Out14 address | 16#3C4A = 15434 | 16#207C/23 | 16#AE/01/23 = 174/01/35 | - | Communication parameters | [always] | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 939
OCAF | Scan.Out15 address | 16#3C4B = 15435 | 16#207C/24 | 16#AE/01/24 = 174/01/36 | - | Communication parameters | [always] | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 940
OCAG | Scan.Out16 address | 16#3C4C = 15436 | 16#207C/25 | 16#AE/01/25 = 174/01/37 | - | Communication parameters | [always] | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 941
OCT | Elc Egy Today | 16#297E = 10622 | 16#204C/17 | 16#96/01/17 = 150/01/23 |  | Actual values parameters | R | UINT (Unsigned32) | - |  | - | [Elc Egy Today] (OCt) | [kWh Counters] ( WC-) [Elec Ener Output Counter] (ELO-) | 942
OCY | Elc Egy Yesterday | 16#2980 = 10624 | 16#204C/19 | 16#96/01/19 = 150/01/25 |  | Actual values parameters | R | UINT (Unsigned32) | - |  | - | [Elc Egy Yesterday] (OCY) | [kWh Counters] ( WC-) [Elec Ener Output Counter] (ELO-) | 943
OE0 | Real Consumption(Wh) | 16#2978 = 10616 | 16#204C/11 | 16#96/01/11 = 150/01/17 | - | Actual values parameters | R/WS | INT (Signed16) | 1 Wh |  | -999 Wh ... 999 Wh | [Real Consumption(Wh)] (OE0) | [Elec Ener Output Counter] (ELO-) | 944
OE1 | Real Consumption(kWh) | 16#2979 = 10617 | 16#204C/12 | 16#96/01/12 = 150/01/18 | - | Actual values parameters | R/WS | INT (Signed16) | 1 kWh |  | -999 kWh ... 999 kWh | [Real Consumption(kWh)] (OE1) | [Elec Ener Output Counter] (ELO-) | 945
OE2 | Real Consumption(MWh) | 16#297A = 10618 | 16#204C/13 | 16#96/01/13 = 150/01/19 | - | Actual values parameters | R/WS | INT (Signed16) | 1 MWh |  | -999 MWh ... 999 MWh | [Real Consumption(MWh)] (OE2) | [Elec Ener Output Counter] (ELO-) | 946
OE3 | Real Consumption(GWh) | 16#297B = 10619 | 16#204C/14 | 16#96/01/14 = 150/01/20 | - | Actual values parameters | R/WS | INT (Signed16) | 1 GWh |  | -999 GWh ... 999 GWh | [Real Consumption(GWh)] (OE3) | [Elec Ener Output Counter] (ELO-) | 947
OE4 | Real Consumption(TWh) | 16#297C = 10620 | 16#204C/15 | 16#96/01/15 = 150/01/21 | - | Actual values parameters | R/WS | INT (Signed16) | 1 TWh |  | -999 TWh ... 999 TWh | [Real Consumption(TWh)] (OE4) | [Elec Ener Output Counter] (ELO-) | 948
OFI | Sinus Filter Activation | 16#0C25 = 3109 | 16#2001/A | 16#70/01/6E = 112/01/110 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Sinus Filter Activation] (OFI) | [Motor monitoring] (MOP-) | 949
OMA7 | Scan. IN7 address | 16#3C2F = 15407 | 16#207C/8 | 16#AE/01/08 = 174/01/08 | - | Communication parameters | [always] | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 950
OMA8 | Scan. IN8 address | 16#3C30 = 15408 | 16#207C/9 | 16#AE/01/09 = 174/01/09 | - | Communication parameters | [always] | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 951
OMA9 | Scan. IN9 address | 16#3C31 = 15409 | 16#207C/A | 16#AE/01/0A = 174/01/10 | - | Communication parameters | [always] | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 952
OMAA | Scan. IN10 address | 16#3C32 = 15410 | 16#207C/B | 16#AE/01/0B = 174/01/11 | - | Communication parameters | [always] | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 953
OMAB | Scan. IN11 address | 16#3C33 = 15411 | 16#207C/C | 16#AE/01/0C = 174/01/12 | - | Communication parameters | [always] | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 954
OMAC | Scan. IN12 address | 16#3C34 = 15412 | 16#207C/D | 16#AE/01/0D = 174/01/13 | - | Communication parameters | [always] | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 955
OMAD | Scan. IN13 address | 16#3C35 = 15413 | 16#207C/E | 16#AE/01/0E = 174/01/14 | - | Communication parameters | [always] | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 956
OMAE | Scan. IN14 address | 16#3C36 = 15414 | 16#207C/F | 16#AE/01/0F = 174/01/15 | - | Communication parameters | [always] | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 957
OMAF | Scan. IN15 address | 16#3C37 = 15415 | 16#207C/10 | 16#AE/01/10 = 174/01/16 | - | Communication parameters | [always] | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 958
OMAG | Scan. IN16 address | 16#3C38 = 15416 | 16#207C/11 | 16#AE/01/11 = 174/01/17 | - | Communication parameters | [always] | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 959
OP0 |  | 16#2973 = 10611 | 16#204C/C | 16#96/01/0C = 150/01/12 | - | Actual values parameters | R/WS | UINT (Unsigned16) | 1 Wh |  | 0 Wh ... 999 Wh |  |  | 960
OP1 |  | 16#2974 = 10612 | 16#204C/D | 16#96/01/0D = 150/01/13 | - | Actual values parameters | R/WS | UINT (Unsigned16) | 1 kWh |  | 0 kWh ... 999 kWh |  |  | 961
OP2 |  | 16#2975 = 10613 | 16#204C/E | 16#96/01/0E = 150/01/14 | - | Actual values parameters | R/WS | UINT (Unsigned16) | 1 MWh |  | 0 MWh ... 999 MWh |  |  | 962
OP3 |  | 16#2976 = 10614 | 16#204C/F | 16#96/01/0F = 150/01/15 | - | Actual values parameters | R/WS | UINT (Unsigned16) | 1 GWh |  | 0 GWh ... 999 GWh |  |  | 963
OP4 |  | 16#2977 = 10615 | 16#204C/10 | 16#96/01/10 = 150/01/16 | - | Actual values parameters | R/WS | UINT (Unsigned16) | 1 TWh |  | 0 TWh ... 999 TWh |  |  | 964
OPPB | OutPresError Resp | 16#3DEF = 15855 | 16#2080/38 | 16#B0/01/38 = 176/01/56 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ramp stop] (rMP) | - | [OutPresError Resp] (OPPb) | [Outlet pressure monitoring] (OPP-) | 965
OPPD | OutPresError Delay | 16#3DEE = 15854 | 16#2080/37 | 16#B0/01/37 = 176/01/55 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | 0 s | 0 s ... 3600 s | [OutPresError Delay] (OPPd) | [Settings] (SEt-) [Outlet pressure monitoring] (OPP-) | 966
OPPH | OutPres Max Level | 16#3DED = 15853 | 16#2080/36 | 16#B0/01/36 = 176/01/54 | - | Configuration and settings | R/W | INT (Signed16) | (call PressureUnitSelected [SUPR]) | (call PressureUnitSelected [SUPR]) | (call PressureUnitSelected [SUPR]) ... (call PressureUnitSelected [SUPR]) | [OutPres Max Level] (OPPH) | [Settings] (SEt-) [Outlet pressure monitoring] (OPP-) | 967
OPPL | OutPres Min Level | 16#3DEC = 15852 | 16#2080/35 | 16#B0/01/35 = 176/01/53 | - | Configuration and settings | R/W | INT (Signed16) | (call PressureUnitSelected [SUPR]) | (call PressureUnitSelected [SUPR]) | (call PressureUnitSelected [SUPR]) ... (call PressureUnitSelected [SUPR]) | [OutPres Min Level] (OPPL) | [Settings] (SEt-) [Outlet pressure monitoring] (OPP-) | 968
OPPM | OutPres Monitoring | 16#3DEA = 15850 | 16#2080/33 | 16#B0/01/33 = 176/01/51 | OPPM | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [OutPres Monitoring] (OPPM) | [Outlet pressure monitoring] (OPP-) | 969
OPPW | OutPres DI Assign | 16#3DEB = 15851 | 16#2080/34 | 16#B0/01/34 = 176/01/52 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Assigned] (nO) | - | [OutPres DI Assign] (OPPW) | [Outlet pressure monitoring] (OPP-) | 970
OPRW | Power Estim Value | 16#0CDC = 3292 | 16#2002/5D | 16#71/01/5D = 113/01/93 | - | Actual values parameters | R | INT (Signed16) | Refer to programming manual |  | Depends of rating | [Power Estim Value] (OPrW) | [Mechanical Energy] (MEC-) | 971
OTP9 | Motor Torque | 16#1CAB = 7339 | 16#202B/28 | 16#85/01/8C = 133/01/140 | - | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % |  |  | 972
OTPA | Motor Torque | 16#1E32 = 7730 | 16#202F/1F | 16#87/01/83 = 135/01/131 | - | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % |  |  | 973
OTPB | Motor Torque | 16#1E33 = 7731 | 16#202F/20 | 16#87/01/84 = 135/01/132 | - | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % |  |  | 974
OTPC | Motor Torque | 16#1E34 = 7732 | 16#202F/21 | 16#87/01/85 = 135/01/133 | - | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % |  |  | 975
OTPD | Motor Torque | 16#1E35 = 7733 | 16#202F/22 | 16#87/01/86 = 135/01/134 | - | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % |  |  | 976
OTPE | Motor Torque | 16#1E36 = 7734 | 16#202F/23 | 16#87/01/87 = 135/01/135 | - | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % |  |  | 977
OTPF | Motor Torque | 16#1E37 = 7735 | 16#202F/24 | 16#87/01/88 = 135/01/136 | - | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % |  |  | 978
PCA | Pump Curve Activate | 16#3D9B = 15771 | 16#207F/48 | 16#AF/01/AC = 175/01/172 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Pump Curve Activate] (PCA) | [Elec Ener Output Counter] (ELO-) | 979
PCAH | Over-Consumption Thd | 16#2A62 = 10850 | 16#204E/33 | 16#97/01/33 = 151/01/51 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 % | 0.0 % | 0.0 % ... 200.0 % | [Over-Consumption Thd] (PCAH) | [Elec Ener Output Counter] (ELO-) | 980
PCAL | Under-Consumption Thd | 16#2A63 = 10851 | 16#204E/34 | 16#97/01/34 = 151/01/52 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 % | 0.0 % | 0.0 % ... 100.0 % | [Under-Consumption Thd] (PCAL) | [Elec Ener Output Counter] (ELO-) | 981
PCAT | Over/Under-Cons Delay | 16#2A64 = 10852 | 16#204E/35 | 16#97/01/35 = 151/01/53 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 min | 1 min | 0 min ... 60 min | [Over/Under-Cons Delay] (PCAt) | [Elec Ener Output Counter] (ELO-) | 982
PCBH | Head BEP | 16#3D97 = 15767 | 16#207F/44 | 16#AF/01/A8 = 175/01/168 | - | Configuration and settings | R/WS | INT (Signed16) | (call PressureUnitSelected [SUPR]) | (call PressureUnitSelected [SUPR]) | (call PressureUnitSelected [SUPR]) ... (call PressureUnitSelected [SUPR]) | [Head BEP] (PCbH) | [Pump characteristics] (PCr-) | 983
PCBP | Power BEP | 16#3D99 = 15769 | 16#207F/46 | 16#AF/01/AA = 175/01/170 | - | Configuration and settings | R/WS | INT (Signed16) | Refer to programming manual | Depends of rating | Depends of rating | [Power BEP] (PCbP) | [Pump characteristics] (PCr-) | 984
PCBQ | Flow at BEP | 16#3D98 = 15768 | 16#207F/45 | 16#AF/01/A9 = 175/01/169 | - | Configuration and settings | R/WS | INT (Signed16) | (call FlowRateUnitSelection [SUFR]) | (call FlowRateUnitSelection [SUFR]) | (call FlowRateUnitSelection [SUFR]) ... (call FlowRateUnitSelection [SUFR]) | [Flow at BEP] (PCbq) | [Pump characteristics] (PCr-) | 985
PCH1 | Head 1 | 16#3D8D = 15757 | 16#207F/3A | 16#AF/01/9E = 175/01/158 | - | Configuration and settings | R/WS | INT (Signed16) | (call PressureUnitSelected [SUPR]) | (call PressureUnitSelected [SUPR]) | (call PressureUnitSelected [SUPR]) ... (call PressureUnitSelected [SUPR]) | [Head 1] (PCH1) | [Pump characteristics] (PCr-) | 986
PCH2 | Head 2 | 16#3D8E = 15758 | 16#207F/3B | 16#AF/01/9F = 175/01/159 | - | Configuration and settings | R/WS | INT (Signed16) | (call PressureUnitSelected [SUPR]) | (call PressureUnitSelected [SUPR]) | (call PressureUnitSelected [SUPR]) ... (call PressureUnitSelected [SUPR]) | [Head 2] (PCH2) | [Pump characteristics] (PCr-) | 987
PCH3 | Head 3 | 16#3D8F = 15759 | 16#207F/3C | 16#AF/01/A0 = 175/01/160 | - | Configuration and settings | R/WS | INT (Signed16) | (call PressureUnitSelected [SUPR]) | (call PressureUnitSelected [SUPR]) | (call PressureUnitSelected [SUPR]) ... (call PressureUnitSelected [SUPR]) | [Head 3] (PCH3) | [Pump characteristics] (PCr-) | 988
PCH4 | Head 4 | 16#3D90 = 15760 | 16#207F/3D | 16#AF/01/A1 = 175/01/161 | - | Configuration and settings | R/WS | INT (Signed16) | (call PressureUnitSelected [SUPR]) | (call PressureUnitSelected [SUPR]) | (call PressureUnitSelected [SUPR]) ... (call PressureUnitSelected [SUPR]) | [Head 4] (PCH4) | [Pump characteristics] (PCr-) | 989
PCH5 | Head 5 | 16#3D91 = 15761 | 16#207F/3E | 16#AF/01/A2 = 175/01/162 | - | Configuration and settings | R/WS | INT (Signed16) | (call PressureUnitSelected [SUPR]) | (call PressureUnitSelected [SUPR]) | (call PressureUnitSelected [SUPR]) ... (call PressureUnitSelected [SUPR]) | [Head 5] (PCH5) | [Pump characteristics] (PCr-) | 990
PCM | Mode | 16#3D9A = 15770 | 16#207F/47 | 16#AF/01/AB = 175/01/171 | PCM | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Mode] (PCM) | [Pump characteristics] (PCr-) | 991
PCP1 | Power 1 | 16#3D92 = 15762 | 16#207F/3F | 16#AF/01/A3 = 175/01/163 | - | Configuration and settings | R/WS | INT (Signed16) | Refer to programming manual | Depends of rating | Depends of rating | [Power 1] (PCP1) | [Pump characteristics] (PCr-) | 992
PCP2 | Power 2 | 16#3D93 = 15763 | 16#207F/40 | 16#AF/01/A4 = 175/01/164 | - | Configuration and settings | R/WS | INT (Signed16) | Refer to programming manual | Depends of rating | Depends of rating | [Power 2] (PCP2) | [Pump characteristics] (PCr-) | 993
PCP3 | Power 3 | 16#3D94 = 15764 | 16#207F/41 | 16#AF/01/A5 = 175/01/165 | - | Configuration and settings | R/WS | INT (Signed16) | Refer to programming manual | Depends of rating | Depends of rating | [Power 3] (PCP3) | [Pump characteristics] (PCr-) | 994
PCP4 | Power 4 | 16#3D95 = 15765 | 16#207F/42 | 16#AF/01/A6 = 175/01/166 | - | Configuration and settings | R/WS | INT (Signed16) | Refer to programming manual | Depends of rating | Depends of rating | [Power 4] (PCP4) | [Pump characteristics] (PCr-) | 995
PCP5 | Power 5 | 16#3D96 = 15766 | 16#207F/43 | 16#AF/01/A7 = 175/01/167 | - | Configuration and settings | R/WS | INT (Signed16) | Refer to programming manual | Depends of rating | Depends of rating | [Power 5] (PCP5) | [Pump characteristics] (PCr-) | 996
PCPB | PumpCycleError Resp | 16#3E1F = 15903 | 16#2081/4 | 16#B0/01/68 = 176/01/104 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ramp stop] (rMP) | - | [PumpCycleError Resp] (PCPb) | [Pumpcycle monitoring] (CSP-) | 997
PCPM | PumpCycle Monitoring | 16#3E1C = 15900 | 16#2081/1 | 16#B0/01/65 = 176/01/101 | PCPM | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [PumpCycle Monitoring] (PCPM) | [Pumpcycle monitoring] (CSP-) | 998
PCPN | PumpCycle MaxStarts | 16#3E1D = 15901 | 16#2081/2 | 16#B0/01/66 = 176/01/102 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 6 | 1 ... 99 | [PumpCycle MaxStarts] (PCPn) | [Settings] (SEt-) [Pumpcycle monitoring] (CSP-) | 999
PCPT | PumpCycle Timeframe | 16#3E1E = 15902 | 16#2081/3 | 16#B0/01/67 = 176/01/103 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 min | 60 min | 0 min ... 3600 min | [PumpCycle Timeframe] (PCPt) | [Settings] (SEt-) [Pumpcycle monitoring] (CSP-) | 1000
PCQ1 | Flow 1 | 16#3D88 = 15752 | 16#207F/35 | 16#AF/01/99 = 175/01/153 | - | Configuration and settings | R/WS | INT (Signed16) | (call FlowRateUnitSelection [SUFR]) | (call FlowRateUnitSelection [SUFR]) | (call FlowRateUnitSelection [SUFR]) ... (call FlowRateUnitSelection [SUFR]) | [Flow 1] (PCq1) | [Pump characteristics] (PCr-) | 1001
PCQ2 | Flow 2 | 16#3D89 = 15753 | 16#207F/36 | 16#AF/01/9A = 175/01/154 | - | Configuration and settings | R/WS | INT (Signed16) | (call FlowRateUnitSelection [SUFR]) | (call FlowRateUnitSelection [SUFR]) | (call FlowRateUnitSelection [SUFR]) ... (call FlowRateUnitSelection [SUFR]) | [Flow 2] (PCq2) | [Pump characteristics] (PCr-) | 1002
PCQ3 | Flow 3 | 16#3D8A = 15754 | 16#207F/37 | 16#AF/01/9B = 175/01/155 | - | Configuration and settings | R/WS | INT (Signed16) | (call FlowRateUnitSelection [SUFR]) | (call FlowRateUnitSelection [SUFR]) | (call FlowRateUnitSelection [SUFR]) ... (call FlowRateUnitSelection [SUFR]) | [Flow 3] (PCq3) | [Pump characteristics] (PCr-) | 1003
PCQ4 | Flow 4 | 16#3D8B = 15755 | 16#207F/38 | 16#AF/01/9C = 175/01/156 | - | Configuration and settings | R/WS | INT (Signed16) | (call FlowRateUnitSelection [SUFR]) | (call FlowRateUnitSelection [SUFR]) | (call FlowRateUnitSelection [SUFR]) ... (call FlowRateUnitSelection [SUFR]) | [Flow 4] (PCq4) | [Pump characteristics] (PCr-) | 1004
PCQ5 | Flow 5 | 16#3D8C = 15756 | 16#207F/39 | 16#AF/01/9D = 175/01/157 | - | Configuration and settings | R/WS | INT (Signed16) | (call FlowRateUnitSelection [SUFR]) | (call FlowRateUnitSelection [SUFR]) | (call FlowRateUnitSelection [SUFR]) ... (call FlowRateUnitSelection [SUFR]) | [Flow 5] (PCq5) | [Pump characteristics] (PCr-) | 1005
PCS | Status | 16#3D86 = 15750 | 16#207F/33 | 16#AF/01/97 = 175/01/151 | PCS | Status parameters | R | WORD (Enumeration) | - |  | - | [Status] (PCS) | [Pump characteristics] (PCr-) | 1006
PCSP | Pump Speed | 16#3D87 = 15751 | 16#207F/34 | 16#AF/01/98 = 175/01/152 | - | Configuration and settings | R/WS | INT (Signed16) | 1 rpm | 0 rpm | 0 rpm ... 32767 rpm | [Pump Speed] (PCSP) | [Pump characteristics] (PCr-) | 1007
PEG | Power Dynamic Gain | 16#3E85 = 16005 | 16#2082/6 | 16#B1/01/06 = 177/01/06 | - | Configuration and settings | R/W | INT (Signed16) | 0.1 % | 0.0 % | -100.0 % ... 100.0 % | [Power Dynamic Gain] (PEG) | [Flow estimation] (SFE-) | 1008
PEO | Power Static Offset | 16#3E86 = 16006 | 16#2082/7 | 16#B1/01/07 = 177/01/07 | - | Configuration and settings | R/W | INT (Signed16) | 0.1 % | 0.0 % | -100.0 % ... 100.0 % | [Power Static Offset] (PEO) | [Flow estimation] (SFE-) | 1009
PEV1 |  | 16#17B6 = 6070 | 16#201E/47 | 16#7F/01/47 = 127/01/71 | PEV1 | Communication parameters | R/WS | WORD (BitString16) | - | 0 | - |  |  | 1010
PEV2 |  | 16#17B7 = 6071 | 16#201E/48 | 16#7F/01/48 = 127/01/72 | PEV2 | Communication parameters | R/WS | WORD (BitString16) | - | 0 | - |  |  | 1011
PEV3 |  | 16#17B8 = 6072 | 16#201E/49 | 16#7F/01/49 = 127/01/73 | PEV3 | Communication parameters | R/WS | WORD (BitString16) | - | 0 | - |  |  | 1012
PEV4 |  | 16#17B9 = 6073 | 16#201E/4A | 16#7F/01/4A = 127/01/74 | PEV4 | Communication parameters | R/WS | WORD (BitString16) | - | 0 | - |  |  | 1013
PFC5 | DI5 Frequency measured | 16#3412 = 13330 | 16#2067/1F | 16#A3/01/83 = 163/01/131 |  | Actual values parameters | R | UINT (Unsigned32) | - |  | - |  |  | 1014
PFC6 | DI6 Frequency measured | 16#3426 = 13350 | 16#2067/33 | 16#A3/01/97 = 163/01/151 |  | Actual values parameters | R | UINT (Unsigned32) | - |  | - |  |  | 1015
PFEC | Activation Source | 16#3DB9 = 15801 | 16#2080/2 | 16#B0/01/02 = 176/01/02 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Yes] (YES) | - | [Activation Source] (PFEC) | [Pipe fill] (PFI-) | 1016
PFHP | Pipe Fill Pressure | 16#3DBC = 15804 | 16#2080/5 | 16#B0/01/05 = 176/01/05 | - | Configuration and settings | R/W | INT (Signed16) | (call PressureUnitSelected [SUPR]) | (call PressureUnitSelected [SUPR]) | (call PressureUnitSelected [SUPR]) ... (call PressureUnitSelected [SUPR]) | [Pipe Fill Pressure] (PFHP) | [Settings] (SEt-) [Pipe fill] (PFI-) | 1017
PFHS | Pipe Fill SPeed | 16#3DBB = 15803 | 16#2080/4 | 16#B0/01/04 = 176/01/04 | - | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | 25.0 Hz | 0.0 Hz ... 599.0 Hz | [Pipe Fill SPeed] (PFHS) | [Settings] (SEt-) [Pipe fill] (PFI-) | 1018
PFHT | Pipe Fill TiMe | 16#3DBA = 15802 | 16#2080/3 | 16#B0/01/03 = 176/01/03 | - | Configuration and settings | R/W | INT (Signed16) | 1 s | 10 s | 0 s ... 32767 s | [Pipe Fill TiMe] (PFHt) | [Settings] (SEt-) [Pipe fill] (PFI-) | 1019
PFI5 | DI5 Frequency Filter | 16#340C = 13324 | 16#2067/19 | 16#A3/01/7D = 163/01/125 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 1000 ms | [DI5 Frequency Filter] (PFI5) | [DI5 Pulse Config] (PAI5-) | 1020
PFI6 | DI6 Frequency Filter | 16#3420 = 13344 | 16#2067/2D | 16#A3/01/91 = 163/01/145 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 1000 ms | [DI6 Frequency Filter] (PFI6) | [DI6 Pulse Config] (PAI6-) | 1021
PFL | U/F Profile | 16#2598 = 9624 | 16#2042/19 | 16#91/01/19 = 145/01/25 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 30 % | 0 % ... 100 % | [U/F Profile] (PFL) | [Motor control] (drC-) | 1022
PFM | Activation Mode | 16#3DB8 = 15800 | 16#2080/1 | 16#B0/01/01 = 176/01/01 | PFM | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Activation Mode] (PFM) | [Pipe fill] (PFI-) | 1023
PFMB | PID Fdbk Error Resp | 16#2E9D = 11933 | 16#2059/22 | 16#9C/01/86 = 156/01/134 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ramp stop] (rMP) | - | [PID Fdbk Error Resp] (PFMb) | [Feedback Monitoring] (F M-) | 1024
PFMD | PID Fdbk Error Delay | 16#2E9C = 11932 | 16#2059/21 | 16#9C/01/85 = 156/01/133 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | 10 s | 0 s ... 3600 s | [PID Fdbk Error Delay] (PFMd) | [Settings] (SEt-) [Feedback Monitoring] (F M-) | 1025
PFMM | PID Fdbk Monitoring | 16#2E9A = 11930 | 16#2059/1F | 16#9C/01/83 = 156/01/131 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [PID Fdbk Monitoring] (PFMM) | [Feedback Monitoring] (F M-) | 1026
PFMR | PID Fdbk Range | 16#2E9B = 11931 | 16#2059/20 | 16#9C/01/84 = 156/01/132 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 3 % | 0 % ... 100 % | [PID Fdbk Range] (PFMr) | [Settings] (SEt-) [Feedback Monitoring] (F M-) | 1027
PHR | Output Ph Rotation | 16#3459 = 13401 | 16#2068/2 | 16#A4/01/02 = 164/01/02 | PHR | Configuration and settings | R/WS | WORD (Enumeration) | - | [ABC] (AbC) | - | [Output Ph Rotation] (PHr) | [Motor control] (drC-) | 1028
PI5J | DI5 Min Process | 16#3414 = 13332 | 16#2067/21 | 16#A3/01/85 = 163/01/133 | - | Configuration and settings | R/WS | INT (Signed16) | 1 | 0 | -32767 ... 32767 | [DI5 Min Process] (PI5J) | [DI5 Pulse Sensor Config] (IF8-) [DI5 Pulse Sensor Config] (HIF8-) [PI5 Installation Flow] (FIF8-) [DI5 Pulse Sensor Config.] (LF8-) [DI5 Pulse Sensor Conf] (bIP5-) [DI5 Pulse Sensor Config] (LIP5-) [DI5 Configuration] (PF8-) [DI5 Pulse Sensor Config] (nPF8-) [DI5 Sensor Config] (SIF8-) | 1029
PI5K | DI5 Max Process | 16#3416 = 13334 | 16#2067/23 | 16#A3/01/87 = 163/01/135 | - | Configuration and settings | R/WS | INT (Signed16) | 1 | 0 | -32767 ... 32767 | [DI5 Max Process] (PI5 ) | [DI5 Pulse Sensor Config] (IF8-) [DI5 Pulse Sensor Config] (HIF8-) [PI5 Installation Flow] (FIF8-) [DI5 Pulse Sensor Config.] (LF8-) [DI5 Pulse Sensor Conf] (bIP5-) [DI5 Pulse Sensor Config] (LIP5-) [DI5 Configuration] (PF8-) [DI5 Pulse Sensor Config] (nPF8-) [DI5 Sensor Config] (SIF8-) | 1030
PI6J | DI6 Min Process | 16#3428 = 13352 | 16#2067/35 | 16#A3/01/99 = 163/01/153 | - | Configuration and settings | R/WS | INT (Signed16) | 1 | 0 | -32767 ... 32767 | [DI6 Min Process] (PI6J) | [DI6 Pulse Sensor Config] (IF9-) [DI6 Pulse Sensor Config] (HIF9-) [PI6 Installation Flow] (FIF9-) [DI6 Pulse Sensor Config.] (LF9-) [DI6 Pulse Sensor Conf] (bIP6-) [DI6 Pulse Sensor Config] (LIP6-) [DI6 Configuration] (PF9-) [DI6 Pulse Sensor Config] (nPF9-) [DI6 Sensor Config] (SIF9-) | 1031
PI6K | DI6 Max Process | 16#342A = 13354 | 16#2067/37 | 16#A3/01/9B = 163/01/155 | - | Configuration and settings | R/WS | INT (Signed16) | 1 | 0 | -32767 ... 32767 | [DI6 Max Process] (PI6 ) | [DI6 Pulse Sensor Config] (IF9-) [DI6 Pulse Sensor Config] (HIF9-) [PI6 Installation Flow] (FIF9-) [DI6 Pulse Sensor Config.] (LF9-) [DI6 Pulse Sensor Conf] (bIP6-) [DI6 Pulse Sensor Config] (LIP6-) [DI6 Configuration] (PF9-) [DI6 Pulse Sensor Config] (nPF9-) [DI6 Sensor Config] (SIF9-) | 1032
PIH5 | DI5 PulseInput High Freq | 16#340A = 13322 | 16#2067/17 | 16#A3/01/7B = 163/01/123 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 kHz | 30.00 kHz | 0.00 kHz ... 30.00 kHz | [DI5 PulseInput High Freq] (PIH5) | [DI5 Pulse Config] (PAI5-) | 1033
PIH6 | DI6 PulseInput High Freq | 16#341E = 13342 | 16#2067/2B | 16#A3/01/8F = 163/01/143 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 kHz | 30.00 kHz | 0.00 kHz ... 30.00 kHz | [DI6 PulseInput High Freq] (PIH6) | [DI6 Pulse Config] (PAI6-) | 1034
PIL5 | DI5 PulseInput Low Freq | 16#3408 = 13320 | 16#2067/15 | 16#A3/01/79 = 163/01/121 |  | Configuration and settings | R/WS | UINT (Unsigned32) | - | 0.00 Hz | - | [DI5 PulseInput Low Freq] (PIL5) | [DI5 Pulse Config] (PAI5-) | 1035
PIL6 | DI6 PulseInput Low Freq | 16#341C = 13340 | 16#2067/29 | 16#A3/01/8D = 163/01/141 |  | Configuration and settings | R/WS | UINT (Unsigned32) | - | 0.00 Hz | - | [DI6 PulseInput Low Freq] (PIL6) | [DI6 Pulse Config] (PAI6-) | 1036
PLFA | PumpLF ActivDelay | 16#3E66 = 15974 | 16#2081/4B | 16#B0/01/AF = 176/01/175 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | 10 s | 0 s ... 3600 s | [PumpLF ActivDelay] (PLFA) | [Settings] (SEt-) [Pump low flow Monit] (PLF-) | 1037
PLFB | PumpLF Error Resp | 16#3E68 = 15976 | 16#2081/4D | 16#B0/01/B1 = 176/01/177 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel Stop] (YES) | - | [PumpLF Error Resp] (PLFb) | [Pump low flow Monit] (PLF-) | 1038
PLFD | PumpLF Error Delay | 16#3E67 = 15975 | 16#2081/4C | 16#B0/01/B0 = 176/01/176 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | 10 s | 0 s ... 3600 s | [PumpLF Error Delay] (PLFd) | [Settings] (SEt-) [Pump low flow Monit] (PLF-) | 1039
PLFL | PumpLF Min Level | 16#3E64 = 15972 | 16#2081/49 | 16#B0/01/AD = 176/01/173 | - | Configuration and settings | R/W | INT (Signed16) | (call FlowRateUnitSelection [SUFR]) | (call FlowRateUnitSelection [SUFR]) | (call FlowRateUnitSelection [SUFR]) ... (call FlowRateUnitSelection [SUFR]) | [PumpLF Min Level] (PLFL) | [Settings] (SEt-) [Pump low flow Monit] (PLF-) | 1040
PLFM | PumpLF Monitoring | 16#3E62 = 15970 | 16#2081/47 | 16#B0/01/AB = 176/01/171 | PLFM | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [PumpLF Monitoring] (PLFM) | [Pump low flow Monit] (PLF-) | 1041
PLFR | PumpLF Restart Delay | 16#3E69 = 15977 | 16#2081/4E | 16#B0/01/B2 = 176/01/178 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | 0 s | 0 s ... 3600 s | [PumpLF Restart Delay] (PLFr) | [Settings] (SEt-) [Pump low flow Monit] (PLF-) | 1042
PLFW | PumpLF DI Assign | 16#3E63 = 15971 | 16#2081/48 | 16#B0/01/AC = 176/01/172 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Assigned] (nO) | - | [PumpLF DI Assign] (PLFW) | [Pump low flow Monit] (PLF-) | 1043
PLFX | PumpLF Power Factor | 16#3E65 = 15973 | 16#2081/4A | 16#B0/01/AE = 176/01/174 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 110 % | 100 % ... 500 % | [PumpLF Power Factor] (PLFX) | [Settings] (SEt-) [Pump low flow Monit] (PLF-) | 1044
PPOA | Priming Pump Assign | 16#3DCC = 15820 | 16#2080/15 | 16#B0/01/15 = 176/01/21 | CSLOUT | Configuration and settings | R/WS | WORD (Enumeration) | - |  | - | [Priming Pump Assign] (PPOA) | [Priming pump ctrl] (PPC-) | 1045
PPSD | Priming Time | 16#3DCD = 15821 | 16#2080/16 | 16#B0/01/16 = 176/01/22 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | 30 s | 0 s ... 3600 s | [Priming Time] (PPSd) | [Settings] (SEt-) [Priming pump ctrl] (PPC-) | 1046
PS1A | InletPres Assign | 16#3D55 = 15701 | 16#207F/2 | 16#AF/01/66 = 175/01/102 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Configured] (nO) | - | [InletPres Assign] (PS1A) | [Sensors Assignment] (SSC-) | 1047
PS1V | Inlet Press. Value | 16#3D61 = 15713 | 16#207F/E | 16#AF/01/72 = 175/01/114 | - | Measurement parameters | R | INT (Signed16) | (call PressureUnitSelected [SUPR]) |  | (call PressureUnitSelected [SUPR]) ... (call PressureUnitSelected [SUPR]) | [Inlet Press. Value] (PS1U) | [Variable Speed Pump] (MPP-) [Display] (SUP-) | 1048
PS2A | OutletPres Assign | 16#3D56 = 15702 | 16#207F/3 | 16#AF/01/67 = 175/01/103 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Configured] (nO) | - | [OutletPres Assign] (PS2A) | [Sensors Assignment] (SSC-) | 1049
PS2V | Outlet Pressure | 16#3D62 = 15714 | 16#207F/F | 16#AF/01/73 = 175/01/115 | - | Measurement parameters | R | INT (Signed16) | (call PressureUnitSelected [SUPR]) |  | (call PressureUnitSelected [SUPR]) ... (call PressureUnitSelected [SUPR]) | [Outlet Pressure] (PS2U) | [Variable Speed Pump] (MPP-) [Display] (SUP-) | 1050
R3 | R3 Assignment | 16#138B = 5003 | 16#2014/4 | 16#7A/01/04 = 122/01/04 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Assigned] (nO) | - | [R3 Assignment] (r3) | [R3 configuration] (r3-) | 1051
R3D | R3 Delay time | 16#1093 = 4243 | 16#200C/2C | 16#76/01/2C = 118/01/44 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [R3 Delay time] (r3d) | [R3 configuration] (r3-) | 1052
R3H | R3 Holding time | 16#107F = 4223 | 16#200C/18 | 16#76/01/18 = 118/01/24 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [R3 Holding time] (r3H) | [R3 configuration] (r3-) | 1053
R3S | R3 Active at | 16#106B = 4203 | 16#200C/4 | 16#76/01/04 = 118/01/04 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [1] (POS) | - | [R3 Active at] (r3S) | [R3 configuration] (r3-) | 1054
R4 | R4 Assignment | 16#138C = 5004 | 16#2014/5 | 16#7A/01/05 = 122/01/05 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Assigned] (nO) | - | [R4 Assignment] (r4) | [R4 configuration] (r4-) | 1055
R4D | R4 Delay time | 16#1094 = 4244 | 16#200C/2D | 16#76/01/2D = 118/01/45 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [R4 Delay time] (r4d) | [R4 configuration] (r4-) | 1056
R4H | R4 Holding time | 16#1080 = 4224 | 16#200C/19 | 16#76/01/19 = 118/01/25 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [R4 Holding time] (r4H) | [R4 configuration] (r4-) | 1057
R4S | R4 Active at | 16#106C = 4204 | 16#200C/5 | 16#76/01/05 = 118/01/05 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [1] (POS) | - | [R4 Active at] (r4S) | [R4 configuration] (r4-) | 1058
R5 | R5 Assignment | 16#138D = 5005 | 16#2014/6 | 16#7A/01/06 = 122/01/06 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Assigned] (nO) | - | [R5 Assignment] (r5) | [R5 configuration] (r5-) | 1059
R5D | R5 Delay time | 16#1095 = 4245 | 16#200C/2E | 16#76/01/2E = 118/01/46 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [R5 Delay time] (r5d) | [R5 configuration] (r5-) | 1060
R5H | R5 Holding time | 16#1081 = 4225 | 16#200C/1A | 16#76/01/1A = 118/01/26 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [R5 Holding time] (r5H) | [R5 configuration] (r5-) | 1061
R5S | R5 Active at | 16#106D = 4205 | 16#200C/6 | 16#76/01/06 = 118/01/06 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [1] (POS) | - | [R5 Active at] (r5S) | [R5 configuration] (r5-) | 1062
R6 | R6 Assignment | 16#138E = 5006 | 16#2014/7 | 16#7A/01/07 = 122/01/07 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Assigned] (nO) | - | [R6 Assignment] (r6) | [R6 configuration] (r6-) | 1063
R6D | R6 activ delay time | 16#1096 = 4246 | 16#200C/2F | 16#76/01/2F = 118/01/47 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [R6 activ delay time] (r6d) | [R6 configuration] (r6-) | 1064
R6H | R6 hold delay time | 16#1082 = 4226 | 16#200C/1B | 16#76/01/1B = 118/01/27 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [R6 hold delay time] (r6H) | [R6 configuration] (r6-) | 1065
R6S | R6 status | 16#106E = 4206 | 16#200C/7 | 16#76/01/07 = 118/01/07 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [1] (POS) | - | [R6 status] (r6S) | [R6 configuration] (r6-) | 1066
RCHT | FlowLim Thd Disable | 16#38B1 = 14513 | 16#2073/E | 16#A9/01/72 = 169/01/114 | - | Configuration and settings | R/W | INT (Signed16) | (call FlowRateUnitSelection [SUFR]) | (call FlowRateUnitSelection [SUFR]) | (call FlowRateUnitSelection [SUFR]) ... (call FlowRateUnitSelection [SUFR]) | [FlowLim Thd Disable] (rCHt) | [Settings] (SEt-) | 1067
RFP9 | Motor frequency | 16#1C5B = 7259 | 16#202A/3C | 16#85/01/3C = 133/01/60 | - | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz |  |  | 1068
RFPA | Motor frequency | 16#1DE2 = 7650 | 16#202E/33 | 16#87/01/33 = 135/01/51 | - | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz |  |  | 1069
RFPB | Motor frequency | 16#1DE3 = 7651 | 16#202E/34 | 16#87/01/34 = 135/01/52 | - | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz |  |  | 1070
RFPC | Motor frequency | 16#1DE4 = 7652 | 16#202E/35 | 16#87/01/35 = 135/01/53 | - | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz |  |  | 1071
RFPD | Motor frequency | 16#1DE5 = 7653 | 16#202E/36 | 16#87/01/36 = 135/01/54 | - | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz |  |  | 1072
RFPE | Motor frequency | 16#1DE6 = 7654 | 16#202E/37 | 16#87/01/37 = 135/01/55 | - | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz |  |  | 1073
RFPF | Motor frequency | 16#1DE7 = 7655 | 16#202E/38 | 16#87/01/38 = 135/01/56 | - | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz |  |  | 1074
RHO | Liquid Density | 16#3E82 = 16002 | 16#2082/3 | 16#B1/01/03 = 177/01/03 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 kg/m³ | 1000 kg/m³ | 100 kg/m³ ... 10000 kg/m³ | [Liquid Density] (rHO) | [Define system units] (SUC-) | 1075
RTD | Reference high Thd | 16#2B05 = 11013 | 16#2050/E | 16#98/01/0E = 152/01/14 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 500.0 Hz | [Reference high Thd] (rtd) | [Threshold reached] (tHrE-) [Settings] (SEt-) | 1076
RTDL | Reference low Thd | 16#2B06 = 11014 | 16#2050/F | 16#98/01/0F = 152/01/15 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 500.0 Hz | [Reference low Thd] (rtdL) | [Threshold reached] (tHrE-) [Settings] (SEt-) | 1077
RTP9 | Run Elapsed time | 16#1C65 = 7269 | 16#202A/46 | 16#85/01/46 = 133/01/70 | - | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h |  |  | 1078
RTPA | Run Elapsed time | 16#1DEC = 7660 | 16#202E/3D | 16#87/01/3D = 135/01/61 | - | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h |  |  | 1079
RTPB | Run Elapsed time | 16#1DED = 7661 | 16#202E/3E | 16#87/01/3E = 135/01/62 | - | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h |  |  | 1080
RTPC | Run Elapsed time | 16#1DEE = 7662 | 16#202E/3F | 16#87/01/3F = 135/01/63 | - | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h |  |  | 1081
RTPD | Run Elapsed time | 16#1DEF = 7663 | 16#202E/40 | 16#87/01/40 = 135/01/64 | - | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h |  |  | 1082
RTPE | Run Elapsed time | 16#1DF0 = 7664 | 16#202E/41 | 16#87/01/41 = 135/01/65 | - | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h |  |  | 1083
RTPF | Run Elapsed time | 16#1DF1 = 7665 | 16#202E/42 | 16#87/01/42 = 135/01/66 | - | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h |  |  | 1084
SAI4 |  | 16#14AE = 5294 | 16#2016/5F | 16#7B/01/5F = 123/01/95 | - | Measurement parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 |  |  | 1085
SAI5 |  | 16#14B2 = 5298 | 16#2016/63 | 16#7B/01/63 = 123/01/99 | - | Measurement parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 |  |  | 1086
SAO2 |  | 16#14B0 = 5296 | 16#2016/61 | 16#7B/01/61 = 123/01/97 | - | Actual values parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 |  |  | 1087
SFP9 | Switching Frequency | 16#1CC9 = 7369 | 16#202B/46 | 16#85/01/AA = 133/01/170 | - | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz |  |  | 1088
SFPA | Switching Frequency | 16#1E50 = 7760 | 16#202F/3D | 16#87/01/A1 = 135/01/161 | - | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz |  |  | 1089
SFPB | Switching Frequency | 16#1E51 = 7761 | 16#202F/3E | 16#87/01/A2 = 135/01/162 | - | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz |  |  | 1090
SFPC | Switching Frequency | 16#1E52 = 7762 | 16#202F/3F | 16#87/01/A3 = 135/01/163 | - | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz |  |  | 1091
SFPD | Switching Frequency | 16#1E53 = 7763 | 16#202F/40 | 16#87/01/A4 = 135/01/164 | - | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz |  |  | 1092
SFPE | Switching Frequency | 16#1E54 = 7764 | 16#202F/41 | 16#87/01/A5 = 135/01/165 | - | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz |  |  | 1093
SFPF | Switching Frequency | 16#1E55 = 7765 | 16#202F/42 | 16#87/01/A6 = 135/01/166 | - | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz |  |  | 1094
SFS | PID Start Ref Freq | 16#2EB3 = 11955 | 16#2059/38 | 16#9C/01/9C = 156/01/156 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 500.0 Hz | [PID Start Ref Freq] (SFS) | [Settings] (SEt-) [Settings] (St-) | 1095
SLBS | SLeep Boost Speed | 16#2DEC = 11756 | 16#2057/39 | 16#9B/01/9D = 155/01/157 | - | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | [No] (nO) | [No] (nO) ... 599.0 Hz | [SLeep Boost Speed] (SLbS) | [Settings] (SEt-) [Boost] (Sbt-) | 1096
SLBT | Sleep Boost Time | 16#2DED = 11757 | 16#2057/3A | 16#9B/01/9E = 155/01/158 | - | Configuration and settings | R/W | INT (Signed16) | 1 s | [No] (nO) | [No] (nO) ... 3600 s | [Sleep Boost Time] (SLbt) | [Settings] (SEt-) [Boost] (Sbt-) | 1097
SLE | Sleep Offset Thres. | 16#2DB6 = 11702 | 16#2057/3 | 16#9B/01/67 = 155/01/103 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 1.0 Hz | 1.0 Hz ... 1000.0 Hz | [Sleep Offset Thres.] (SLE) | [Stop after speed timeout] (PrSP-) [Settings] (SEt-) | 1098
SLFV | Estimated Pump Flow | 16#3E87 = 16007 | 16#2082/8 | 16#B1/01/08 = 177/01/08 | - | Actual values parameters | R | INT (Signed16) | (call FlowRateUnitSelection [SUFR]) |  | (call FlowRateUnitSelection [SUFR]) ... (call FlowRateUnitSelection [SUFR]) | [Estimated Pump Flow] (SLFU) | [Control] (Ctr-) [Flow estimation] (SFE-) | 1099
SLHV | Head Estimated | 16#3E8C = 16012 | 16#2082/D | 16#B1/01/0D = 177/01/13 | - | Actual values parameters | R | INT (Signed16) | (call PressureUnitSelected [SUPR]) |  | (call PressureUnitSelected [SUPR]) ... (call PressureUnitSelected [SUPR]) | [Head Estimated] (SLHU) | [Pump characteristics] (PCr-) | 1100
SLNL | Sleep Flow Level | 16#2DE8 = 11752 | 16#2057/35 | 16#9B/01/99 = 155/01/153 | - | Actual values parameters | R/W | INT (Signed16) | (call FlowRateUnitSelection [SUFR]) | [No] (nO) | [No] (nO) ... (call FlowRateUnitSelection [SUFR]) | [Sleep Flow Level] (SLnL) | [Settings] (SEt-) [Sleep menu] (SLP-) | 1101
SLPD | Sleep Delay | 16#2DEB = 11755 | 16#2057/38 | 16#9B/01/9C = 155/01/156 | - | Actual values parameters | R/W | INT (Signed16) | 1 s | 20 s | 0 s ... 3600 s | [Sleep Delay] (SLPd) | [Settings] (SEt-) [Sleep menu] (SLP-) | 1102
SLPM | Sleep Detect Mode | 16#2DE6 = 11750 | 16#2057/33 | 16#9B/01/97 = 155/01/151 | SLPM | Actual values parameters | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Sleep Detect Mode] (SLPM) | [Sleep menu] (SLP-) | 1103
SLPR | Sleep Power Level | 16#2DEA = 11754 | 16#2057/37 | 16#9B/01/9B = 155/01/155 | - | Actual values parameters | R/W | INT (Signed16) | Refer to programming manual | [No] (nO) | Depends of rating | [Sleep Power Level] (SLPr) | [Settings] (SEt-) [Sleep menu] (SLP-) | 1104
SLPW | Sleep Switch Assign | 16#2DE7 = 11751 | 16#2057/34 | 16#9B/01/98 = 155/01/152 | PSLIN | Actual values parameters | R/WS | WORD (Enumeration) | - | [Not Assigned] (nO) | - | [Sleep Switch Assign] (SLPW) | [Sleep menu] (SLP-) | 1105
SLSL | Sleep Min Speed | 16#2DE9 = 11753 | 16#2057/36 | 16#9B/01/9A = 155/01/154 | - | Actual values parameters | R/W | INT (Signed16) | 0.1 Hz | [No] (nO) | [No] (nO) ... 599.0 Hz | [Sleep Min Speed] (SLSL) | [Settings] (SEt-) [Sleep menu] (SLP-) | 1106
SPD | Motor Speed | 16#2EE4 = 12004 | 16#205A/5 | 16#9D/01/05 = 157/01/05 | - | Actual values parameters | R | UINT (Unsigned16) | Refer to programming manual |  | Refer to programming manual | [Motor Speed] (SPd) | [Pump Dashboard] (PMt-) [Fan Dashboard] (FAn-) [Motor parameters] (MMO-) [Display] (SUP-) | 1107
ST00 |  | 16#3EE4 = 16100 | 16#2083/1 | 16#B1/01/65 = 177/01/101 | ST00 | Status parameters | R | WORD (BitString16) | - |  | - |  |  | 1108
ST02 |  | 16#3EE6 = 16102 | 16#2083/3 | 16#B1/01/67 = 177/01/103 | ST02 | Status parameters | R | WORD (BitString16) | - |  | - |  |  | 1109
ST03 |  | 16#3EE7 = 16103 | 16#2083/4 | 16#B1/01/68 = 177/01/104 | ST03 | Status parameters | R | WORD (BitString16) | - |  | - |  |  | 1110
ST04 |  | 16#3EE8 = 16104 | 16#2083/5 | 16#B1/01/69 = 177/01/105 | ST04 | Status parameters | R | WORD (BitString16) | - |  | - |  |  | 1111
ST05 |  | 16#3EE9 = 16105 | 16#2083/6 | 16#B1/01/6A = 177/01/106 | ST05 | Status parameters | R | WORD (BitString16) | - |  | - |  |  | 1112
ST06 |  | 16#3EEA = 16106 | 16#2083/7 | 16#B1/01/6B = 177/01/107 | ST06 | Status parameters | R | WORD (BitString16) | - |  | - |  |  | 1113
ST07 |  | 16#3EEB = 16107 | 16#2083/8 | 16#B1/01/6C = 177/01/108 | ST07 | Status parameters | R | WORD (BitString16) | - |  | - |  |  | 1114
ST08 |  | 16#3EEC = 16108 | 16#2083/9 | 16#B1/01/6D = 177/01/109 | ST08 | Status parameters | R | WORD (BitString16) | - |  | - |  |  | 1115
ST09 |  | 16#3EED = 16109 | 16#2083/A | 16#B1/01/6E = 177/01/110 | ST09 | Status parameters | R | WORD (BitString16) | - |  | - |  |  | 1116
ST11 |  | 16#3EEF = 16111 | 16#2083/C | 16#B1/01/70 = 177/01/112 | ST11 | Status parameters | R | WORD (BitString16) | - |  | - |  |  | 1117
ST12 |  | 16#3EF0 = 16112 | 16#2083/D | 16#B1/01/71 = 177/01/113 | ST12 | Status parameters | R | WORD (BitString16) | - |  | - |  |  | 1118
ST13 |  | 16#3EF1 = 16113 | 16#2083/E | 16#B1/01/72 = 177/01/114 | ST13 | Status parameters | R | WORD (BitString16) | - |  | - |  |  | 1119
ST14 |  | 16#3EF2 = 16114 | 16#2083/F | 16#B1/01/73 = 177/01/115 | ST14 | Status parameters | R | WORD (BitString16) | - |  | - |  |  | 1120
ST15 |  | 16#3EF3 = 16115 | 16#2083/10 | 16#B1/01/74 = 177/01/116 | ST15 | Status parameters | R | WORD (BitString16) | - |  | - |  |  | 1121
ST16 |  | 16#3EF4 = 16116 | 16#2083/11 | 16#B1/01/75 = 177/01/117 | ST16 | Status parameters | R | WORD (BitString16) | - |  | - |  |  | 1122
ST17 |  | 16#3EF5 = 16117 | 16#2083/12 | 16#B1/01/76 = 177/01/118 | ST17 | Status parameters | R | WORD (BitString16) | - |  | - |  |  | 1123
ST18 |  | 16#3EF6 = 16118 | 16#2083/13 | 16#B1/01/77 = 177/01/119 | ST18 | Status parameters | R | WORD (BitString16) | - |  | - |  |  | 1124
ST19 |  | 16#3EF7 = 16119 | 16#2083/14 | 16#B1/01/78 = 177/01/120 | ST19 | Status parameters | R | WORD (BitString16) | - |  | - |  |  | 1125
STOF | STOx Input State | 16#3BDB = 15323 | 16#207B/18 | 16#AD/01/7C = 173/01/124 | - | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 1126
STP1 | Stall Max Time | 16#2437 = 9271 | 16#203E/48 | 16#8F/01/48 = 143/01/72 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 60.0 s | 0.0 s ... 200.0 s | [Stall Max Time] (StP1) | [Stall monitoring] (StPr-) [Settings] (SEt-) | 1127
STP2 | Stall Current | 16#2438 = 9272 | 16#203E/49 | 16#8F/01/49 = 143/01/73 | - | Configuration and settings | R/W | INT (Signed16) | 0.1 % | 150.0 % | 0.0 % ... 150.0 % | [Stall Current] (StP2) | [Stall monitoring] (StPr-) [Settings] (SEt-) | 1128
STP3 | Stall Frequency | 16#2439 = 9273 | 16#203E/4A | 16#8F/01/4A = 143/01/74 | - | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | 2.0 Hz | 0.0 Hz ... 500.0 Hz | [Stall Frequency] (StP3) | [Stall monitoring] (StPr-) [Settings] (SEt-) | 1129
STPC | Stall Monitoring | 16#2436 = 9270 | 16#203E/47 | 16#8F/01/47 = 143/01/71 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Stall Monitoring] (StPC) | [Stall monitoring] (StPr-) | 1130
SUCU | Currency unit list | 16#2EF9 = 12025 | 16#205A/1A | 16#9D/01/1A = 157/01/26 | SUCU | Status parameters | R/WS | WORD (Enumeration) | - | Refer to programming manual | - | [Currency unit list] (SUCU) | [Define system units] (SUC-) | 1131
SUFR | Flow rate unit | 16#2EF6 = 12022 | 16#205A/17 | 16#9D/01/17 = 157/01/23 | SUFR | Status parameters | R/WS | WORD (Enumeration) | - | Refer to programming manual | - | [Flow rate unit] (SUFr) | [Define system units] (SUC-) | 1132
SUPR | P sensor unit | 16#2EF5 = 12021 | 16#205A/16 | 16#9D/01/16 = 157/01/22 | SUPR | Status parameters | R/WS | WORD (Enumeration) | - | Refer to programming manual | - | [P sensor unit] (SUPr) | [Define system units] (SUC-) | 1133
SUTP | Temperature unit | 16#2EF8 = 12024 | 16#205A/19 | 16#9D/01/19 = 157/01/25 | SUTP | Status parameters | R/WS | WORD (Enumeration) | - | Refer to programming manual | - | [Temperature unit] (SUtP) | [Define system units] (SUC-) | 1134
TBR2 | HMI baud rate | 16#1787 = 6023 | 16#201E/18 | 16#7F/01/18 = 127/01/24 | TBR | Configuration and settings | R/WS | WORD (Enumeration) | - | [19200 bps] (19 2) | - | [HMI baud rate] (tbr2) | [Modbus HMI] (Md2-) | 1135
TDP9 | Drive Thermal State | 16#1CB5 = 7349 | 16#202B/32 | 16#85/01/96 = 133/01/150 | - | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 % |  |  | 1136
TDPA | Drive Thermal State | 16#1E3C = 7740 | 16#202F/29 | 16#87/01/8D = 135/01/141 | - | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 % |  |  | 1137
TDPB | Drive Thermal State | 16#1E3D = 7741 | 16#202F/2A | 16#87/01/8E = 135/01/142 | - | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 % |  |  | 1138
TDPC | Drive Thermal State | 16#1E3E = 7742 | 16#202F/2B | 16#87/01/8F = 135/01/143 | - | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 % |  |  | 1139
TDPD | Drive Thermal State | 16#1E3F = 7743 | 16#202F/2C | 16#87/01/90 = 135/01/144 | - | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 % |  |  | 1140
TDPE | Drive Thermal State | 16#1E40 = 7744 | 16#202F/2D | 16#87/01/91 = 135/01/145 | - | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 % |  |  | 1141
TDPF | Drive Thermal State | 16#1E41 = 7745 | 16#202F/2E | 16#87/01/92 = 135/01/146 | - | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 % |  |  | 1142
TFO2 | HMI format | 16#1788 = 6024 | 16#201E/19 | 16#7F/01/19 = 127/01/25 | FOR | Configuration and settings | R/WS | WORD (Enumeration) | - | [8-E-1] (8E1) | - | [HMI format] (tFO2) | [Modbus HMI] (Md2-) | 1143
TH2A | AI2 Th Warn Level | 16#33A4 = 13220 | 16#2066/15 | 16#A3/01/15 = 163/01/21 | - | Configuration and settings | R/W | INT (Signed16) | (call TemperatureUnitSelection [SUTP]) | Refer to programming manual | (call TemperatureUnitSelection [SUTP]) ... (call TemperatureUnitSelection [SUTP]) | [AI2 Th Warn Level] (tH2A) | [Settings] (SEt-) [Thermal monitoring] (tPP-) | 1144
TH2B | AI2 Th Error Resp | 16#33B8 = 13240 | 16#2066/29 | 16#A3/01/29 = 163/01/41 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ramp stop] (rMP) | - | [AI2 Th Error Resp] (tH2b) | [Thermal monitoring] (tPP-) | 1145
TH2F | AI2 Th Error Level | 16#33AE = 13230 | 16#2066/1F | 16#A3/01/1F = 163/01/31 | - | Configuration and settings | R/W | INT (Signed16) | (call TemperatureUnitSelection [SUTP]) | Refer to programming manual | (call TemperatureUnitSelection [SUTP]) ... (call TemperatureUnitSelection [SUTP]) | [AI2 Th Error Level] (tH2F) | [Settings] (SEt-) [Thermal monitoring] (tPP-) | 1146
TH2S | AI2 Th Monitoring | 16#339A = 13210 | 16#2066/B | 16#A3/01/0B = 163/01/11 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [AI2 Th Monitoring] (tH2S) | [Thermal monitoring] (tPP-) | 1147
TH2V | AI2 Th Value | 16#33C2 = 13250 | 16#2066/33 | 16#A3/01/33 = 163/01/51 | - | Measurement parameters | R | INT (Signed16) | (call TemperatureUnitSelection [SUTP]) |  | (call TemperatureUnitSelection [SUTP]) ... (call TemperatureUnitSelection [SUTP]) | [AI2 Th Value] (tH2U) | [Thermal Monitoring] (tPM-) [Thermal monitoring] (tPP-) [Display] (SUP-) | 1148
TH3A | AI3 Th Warn Level | 16#33A5 = 13221 | 16#2066/16 | 16#A3/01/16 = 163/01/22 | - | Configuration and settings | R/W | INT (Signed16) | (call TemperatureUnitSelection [SUTP]) | Refer to programming manual | (call TemperatureUnitSelection [SUTP]) ... (call TemperatureUnitSelection [SUTP]) | [AI3 Th Warn Level] (tH3A) | [Settings] (SEt-) [Thermal monitoring] (tPP-) | 1149
TH3B | AI3 Th Error Resp | 16#33B9 = 13241 | 16#2066/2A | 16#A3/01/2A = 163/01/42 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ramp stop] (rMP) | - | [AI3 Th Error Resp] (tH3b) | [Thermal monitoring] (tPP-) | 1150
TH3F | AI3 Th Error Level | 16#33AF = 13231 | 16#2066/20 | 16#A3/01/20 = 163/01/32 | - | Configuration and settings | R/W | INT (Signed16) | (call TemperatureUnitSelection [SUTP]) | Refer to programming manual | (call TemperatureUnitSelection [SUTP]) ... (call TemperatureUnitSelection [SUTP]) | [AI3 Th Error Level] (tH3F) | [Settings] (SEt-) [Thermal monitoring] (tPP-) | 1151
TH3S | AI3 Th Monitoring | 16#339B = 13211 | 16#2066/C | 16#A3/01/0C = 163/01/12 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [AI3 Th Monitoring] (tH3S) | [Thermal monitoring] (tPP-) | 1152
TH3V | AI3 Th Value | 16#33C3 = 13251 | 16#2066/34 | 16#A3/01/34 = 163/01/52 | - | Measurement parameters | R | INT (Signed16) | (call TemperatureUnitSelection [SUTP]) |  | (call TemperatureUnitSelection [SUTP]) ... (call TemperatureUnitSelection [SUTP]) | [AI3 Th Value] (tH3U) | [Thermal Monitoring] (tPM-) [Thermal monitoring] (tPP-) [Display] (SUP-) | 1153
TH4A | AI4 Th Warn Level | 16#33A6 = 13222 | 16#2066/17 | 16#A3/01/17 = 163/01/23 | - | Configuration and settings | R/W | INT (Signed16) | (call TemperatureUnitSelection [SUTP]) | Refer to programming manual | (call TemperatureUnitSelection [SUTP]) ... (call TemperatureUnitSelection [SUTP]) | [AI4 Th Warn Level] (tH4A) | [Settings] (SEt-) [Thermal monitoring] (tPP-) | 1154
TH4B | AI4 Th Error Resp | 16#33BA = 13242 | 16#2066/2B | 16#A3/01/2B = 163/01/43 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ramp stop] (rMP) | - | [AI4 Th Error Resp] (tH4b) | [Thermal monitoring] (tPP-) | 1155
TH4F | AI4 Th Error Level | 16#33B0 = 13232 | 16#2066/21 | 16#A3/01/21 = 163/01/33 | - | Configuration and settings | R/W | INT (Signed16) | (call TemperatureUnitSelection [SUTP]) | Refer to programming manual | (call TemperatureUnitSelection [SUTP]) ... (call TemperatureUnitSelection [SUTP]) | [AI4 Th Error Level] (tH4F) | [Settings] (SEt-) [Thermal monitoring] (tPP-) | 1156
TH4S | AI4 Th Monitoring | 16#339C = 13212 | 16#2066/D | 16#A3/01/0D = 163/01/13 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [AI4 Th Monitoring] (tH4S) | [Thermal monitoring] (tPP-) | 1157
TH4V | AI4 Th Value | 16#33C4 = 13252 | 16#2066/35 | 16#A3/01/35 = 163/01/53 | - | Measurement parameters | R | INT (Signed16) | (call TemperatureUnitSelection [SUTP]) |  | (call TemperatureUnitSelection [SUTP]) ... (call TemperatureUnitSelection [SUTP]) | [AI4 Th Value] (tH4U) | [Thermal Monitoring] (tPM-) [Thermal monitoring] (tPP-) [Display] (SUP-) | 1158
TH5A | AI5 Th Warn Level | 16#33A7 = 13223 | 16#2066/18 | 16#A3/01/18 = 163/01/24 | - | Configuration and settings | R/W | INT (Signed16) | (call TemperatureUnitSelection [SUTP]) | Refer to programming manual | (call TemperatureUnitSelection [SUTP]) ... (call TemperatureUnitSelection [SUTP]) | [AI5 Th Warn Level] (tH5A) | [Settings] (SEt-) [Thermal monitoring] (tPP-) | 1159
TH5B | AI5 Th Error Resp | 16#33BB = 13243 | 16#2066/2C | 16#A3/01/2C = 163/01/44 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ramp stop] (rMP) | - | [AI5 Th Error Resp] (tH5b) | [Thermal monitoring] (tPP-) | 1160
TH5F | AI5 Th Error Level | 16#33B1 = 13233 | 16#2066/22 | 16#A3/01/22 = 163/01/34 | - | Configuration and settings | R/W | INT (Signed16) | (call TemperatureUnitSelection [SUTP]) | Refer to programming manual | (call TemperatureUnitSelection [SUTP]) ... (call TemperatureUnitSelection [SUTP]) | [AI5 Th Error Level] (tH5F) | [Settings] (SEt-) [Thermal monitoring] (tPP-) | 1161
TH5S | AI5 Th Monitoring | 16#339D = 13213 | 16#2066/E | 16#A3/01/0E = 163/01/14 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [AI5 Th Monitoring] (tH5S) | [Thermal monitoring] (tPP-) | 1162
TH5V | AI5 Th Value | 16#33C5 = 13253 | 16#2066/36 | 16#A3/01/36 = 163/01/54 | - | Measurement parameters | R | INT (Signed16) | (call TemperatureUnitSelection [SUTP]) |  | (call TemperatureUnitSelection [SUTP]) ... (call TemperatureUnitSelection [SUTP]) | [AI5 Th Value] (tH5U) | [Thermal Monitoring] (tPM-) [Thermal monitoring] (tPP-) [Display] (SUP-) | 1163
THP9 | Motor therm state | 16#1C79 = 7289 | 16#202A/5A | 16#85/01/5A = 133/01/90 | - | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % |  |  | 1164
THPA | Motor therm state | 16#1E00 = 7680 | 16#202E/51 | 16#87/01/51 = 135/01/81 | - | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % |  |  | 1165
THPB | Motor therm state | 16#1E01 = 7681 | 16#202E/52 | 16#87/01/52 = 135/01/82 | - | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % |  |  | 1166
THPC | Motor therm state | 16#1E02 = 7682 | 16#202E/53 | 16#87/01/53 = 135/01/83 | - | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % |  |  | 1167
THPD | Motor therm state | 16#1E03 = 7683 | 16#202E/54 | 16#87/01/54 = 135/01/84 | - | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % |  |  | 1168
THPE | Motor therm state | 16#1E04 = 7684 | 16#202E/55 | 16#87/01/55 = 135/01/85 | - | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % |  |  | 1169
THPF | Motor therm state | 16#1E05 = 7685 | 16#202E/56 | 16#87/01/56 = 135/01/86 | - | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % |  |  | 1170
TJP9 | IGBT Junction Temp | 16#1CBF = 7359 | 16#202B/3C | 16#85/01/A0 = 133/01/160 | - | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C |  |  | 1171
TJPA | IGBT Junction Temp | 16#1E46 = 7750 | 16#202F/33 | 16#87/01/97 = 135/01/151 | - | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C |  |  | 1172
TJPB | IGBT Junction Temp | 16#1E47 = 7751 | 16#202F/34 | 16#87/01/98 = 135/01/152 | - | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C |  |  | 1173
TJPC | IGBT Junction Temp | 16#1E48 = 7752 | 16#202F/35 | 16#87/01/99 = 135/01/153 | - | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C |  |  | 1174
TJPD | IGBT Junction Temp | 16#1E49 = 7753 | 16#202F/36 | 16#87/01/9A = 135/01/154 | - | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C |  |  | 1175
TJPE | IGBT Junction Temp | 16#1E4A = 7754 | 16#202F/37 | 16#87/01/9B = 135/01/155 | - | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C |  |  | 1176
TJPF | IGBT Junction Temp | 16#1E4B = 7755 | 16#202F/38 | 16#87/01/9C = 135/01/156 | - | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C |  |  | 1177
TOCT | Type of control | 16#2E8F = 11919 | 16#2059/14 | 16#9C/01/78 = 156/01/120 | TOCT | Configuration and settings | R/WS | WORD (Enumeration) | - | [NA] (nA) | - | [Type of control] (tOCt) | [Feedback] (Fdb-) | 1178
TQS | Nom Motor torque | 16#25D4 = 9684 | 16#2042/55 | 16#91/01/55 = 145/01/85 | - | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | Depends of rating | Depends of rating | [Nom Motor torque] (tqS) | [data] (Mtd-) | 1179
TTOB |  | 16#FB9F = 64415 |  | = | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 s | 10.0 s | 0.1 s ... 30.0 s |  |  | 1180
UIH3 | AI3 Max Value | 16#1148 = 4424 | 16#200E/19 | 16#77/01/19 = 119/01/25 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 10.0 V | 0.0 V ... 10.0 V | [AI3 Max Value] (UIH3) | [Feedback] (Fdb-) | 1181
UIH4 | AI4 Max Value | 16#1149 = 4425 | 16#200E/1A | 16#77/01/1A = 119/01/26 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 10.0 V | 0.0 V ... 10.0 V | [AI4 Max Value] (UIH4) | [Feedback] (Fdb-) | 1182
UIH5 | AI5 volt scl prm 100% | 16#114A = 4426 | 16#200E/1B | 16#77/01/1B = 119/01/27 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 10.0 V | 0.0 V ... 10.0 V | [AI5 volt scl prm 100%] (UIH5) | [Feedback] (Fdb-) | 1183
UIL3 | AI3 Min. Value | 16#113E = 4414 | 16#200E/F | 16#77/01/0F = 119/01/15 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 0.0 V | 0.0 V ... 10.0 V | [AI3 Min. Value] (UIL3) | [Feedback] (Fdb-) | 1184
UIL4 | AI4 Min. Value | 16#113F = 4415 | 16#200E/10 | 16#77/01/10 = 119/01/16 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 0.0 V | 0.0 V ... 10.0 V | [AI4 Min. Value] (UIL4) | [Feedback] (Fdb-) | 1185
UIL5 | AI5 volt scl prm 0% | 16#1140 = 4416 | 16#200E/11 | 16#77/01/11 = 119/01/17 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 0.0 V | 0.0 V ... 10.0 V | [AI5 volt scl prm 0%] (UIL5) | [Feedback] (Fdb-) | 1186
ULP9 | Mains voltage | 16#1C6F = 7279 | 16#202A/50 | 16#85/01/50 = 133/01/80 | - | History parameters | R | UINT (Unsigned16) | 0.1 V |  | [No meas.] (----) ... 6553.5 V |  |  | 1187
ULPA | Mains voltage | 16#1DF6 = 7670 | 16#202E/47 | 16#87/01/47 = 135/01/71 | - | History parameters | R | UINT (Unsigned16) | 0.1 V |  | [No meas.] (----) ... 6553.5 V |  |  | 1188
ULPB | Mains voltage | 16#1DF7 = 7671 | 16#202E/48 | 16#87/01/48 = 135/01/72 | - | History parameters | R | UINT (Unsigned16) | 0.1 V |  | [No meas.] (----) ... 6553.5 V |  |  | 1189
ULPC | Mains voltage | 16#1DF8 = 7672 | 16#202E/49 | 16#87/01/49 = 135/01/73 | - | History parameters | R | UINT (Unsigned16) | 0.1 V |  | [No meas.] (----) ... 6553.5 V |  |  | 1190
ULPD | Mains voltage | 16#1DF9 = 7673 | 16#202E/4A | 16#87/01/4A = 135/01/74 | - | History parameters | R | UINT (Unsigned16) | 0.1 V |  | [No meas.] (----) ... 6553.5 V |  |  | 1191
ULPE | Mains voltage | 16#1DFA = 7674 | 16#202E/4B | 16#87/01/4B = 135/01/75 | - | History parameters | R | UINT (Unsigned16) | 0.1 V |  | [No meas.] (----) ... 6553.5 V |  |  | 1192
ULPF | Mains voltage | 16#1DFB = 7675 | 16#202E/4C | 16#87/01/4C = 135/01/76 | - | History parameters | R | UINT (Unsigned16) | 0.1 V |  | [No meas.] (----) ... 6553.5 V |  |  | 1193
UOH2 | AQ2 max Output | 16#1218 = 4632 | 16#2010/21 | 16#78/01/21 = 120/01/33 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 10.0 V | 0.0 V ... 10.0 V | [AQ2 max Output] (UOH2) | [AQ2 configuration] (AO2-) | 1194
UOL2 | AQ2 min Output | 16#120E = 4622 | 16#2010/17 | 16#78/01/17 = 120/01/23 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 0.0 V | 0.0 V ... 10.0 V | [AQ2 min Output] (UOL2) | [AQ2 configuration] (AO2-) | 1195
VBUS | DC bus voltage | 16#0CAB = 3243 | 16#2002/2C | 16#71/01/2C = 113/01/44 | - | Measurement parameters | R | UINT (Unsigned16) | 0.1 V |  | 0 ... 65535 | [DC bus voltage] (UbUS) | [Drive parameters] (MPI-) [Display] (SUP-) | 1196
VCB | Catch on Fly Sensitivity | 16#0C27 = 3111 | 16#2001/C | 16#70/01/70 = 112/01/112 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 V | 0.20 V | 0.10 V ... 100.00 V | [Catch on Fly Sensitivity] (UCb) | [Catch on the fly] (FLr-) | 1197
WUPE | Wake Up Process Error | 16#2DF0 = 11760 | 16#2057/3D | 16#9B/01/A1 = 155/01/161 | - | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | Refer to programming manual | Refer to programming manual | [Wake Up Process Error] (WUPE) | [Settings] (SEt-) [Wake up menu] (W P-) | 1198
WUPF | Wake Up Process level | 16#2DEF = 11759 | 16#2057/3C | 16#9B/01/A0 = 155/01/160 | - | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | Refer to programming manual | Refer to programming manual | [Wake Up Process level] (WUPF) | [Settings] (SEt-) [Wake up menu] (W P-) | 1199
WUPM | Wake Up Mode | 16#2DEE = 11758 | 16#2057/3B | 16#9B/01/9F = 155/01/159 | WUPM | Configuration and settings | R/WS | WORD (Enumeration) | - | [FeedBack] (Fb ) | - | [Wake Up Mode] (WUPM) | [Wake up menu] (W P-) | 1200
PREF | Reference Power | 16#2A30 = 10800 | 16#204E/1 | 16#97/01/01 = 151/01/01 | - | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | Depends of rating | Depends of rating | [Reference Power] (PrEF) | [Energy Saving] (ESA-) | 1201
EPR |  | 16#0CE1 = 3297 | 16#2002/62 | 16#71/01/62 = 113/01/98 | - | Actual values parameters | R | INT (Signed16) | 1 % |  | -300 % ... 300 % | (EPr) | [kWh Counters] ( WC-) [Elec Ener Output Counter] (ELO-) [Variable Speed Pump] (MPP-) [Display] (SUP-) | 1202
AV1J | AIV1 Lowest Process | 16#11AA = 4522 | 16#200F/17 | 16#77/01/7B = 119/01/123 | - | Configuration and settings | R/WS | INT (Signed16) | 1 | 0 | -32767 ... 32767 | [AIV1 Lowest Process] (AU1J) | [AIV1 Sensor Config.] (ICU1-) [AIV1 Sensor Config.] (OCU1-) [AIV1 Sensor Config.] (IFU1-) [AIV1 Sensor Config.] (HIU1-) [AIV1 Sensor Config.] (FIU1-) [AIV1 Sensor Config.] (LFU1-) [AIV1 Sensor Config.] (bIU1-) [AIV1 Configuration] (LIU1-) [AIV1 Configuration] (PFU1-) [AIV1 Sensor Config.] (nPU1-) [AIV1 Sensor Config.] (IPU1-) [AIV1 Configuration] (PPU1-) [AIV1 Sensor Config.] (OOU1-) [AIV1 Configuration] (LCU1-) [AIV1 Sensor Config.] (LSU1-) [AIV1 Sensor Config.] (SIU1-) [AIV1 Sensor Config.] (SOU1-) [AIV1 Sensor Config.] (WOU1-) [AIV1 Sensor Config.] (PF1U-) | 1203
AV1K | AIV1 Highest Process | 16#11B4 = 4532 | 16#200F/21 | 16#77/01/85 = 119/01/133 | - | Configuration and settings | R/WS | INT (Signed16) | 1 | 0 | -32767 ... 32767 | [AIV1 Highest Process] (AU1 ) | [AIV1 Sensor Config.] (ICU1-) [AIV1 Sensor Config.] (OCU1-) [AIV1 Sensor Config.] (IFU1-) [AIV1 Sensor Config.] (HIU1-) [AIV1 Sensor Config.] (FIU1-) [AIV1 Sensor Config.] (LFU1-) [AIV1 Sensor Config.] (bIU1-) [AIV1 Configuration] (LIU1-) [AIV1 Configuration] (PFU1-) [AIV1 Sensor Config.] (nPU1-) [AIV1 Sensor Config.] (IPU1-) [AIV1 Configuration] (PPU1-) [AIV1 Sensor Config.] (OOU1-) [AIV1 Configuration] (LCU1-) [AIV1 Sensor Config.] (LSU1-) [AIV1 Sensor Config.] (SIU1-) [AIV1 Sensor Config.] (SOU1-) [AIV1 Sensor Config.] (WOU1-) [AIV1 Sensor Config.] (PF1U-) | 1204
SPDM | Motor Mechanical speed | 16#2EEB = 12011 | 16#205A/C | 16#9D/01/0C = 157/01/12 | - | Actual values parameters | R | UINT (Unsigned16) | Refer to programming manual |  | Refer to programming manual | [Motor Mechanical speed] (SPdM) | [Variable Speed Pump] (MPP-) | 1205
DRC9 | Ref Freq Channel | 16#FB3F = 64319 |  | = | CNL | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 1206
DRCA | Ref Freq Channel | 16#FB40 = 64320 |  | = | CNL | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 1207
DRCB | Ref Freq Channel | 16#FB41 = 64321 |  | = | CNL | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 1208
DRCC | Ref Freq Channel | 16#FB42 = 64322 |  | = | CNL | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 1209
DRCD | Ref Freq Channel | 16#FB43 = 64323 |  | = | CNL | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 1210
DRCE | Ref Freq Channel | 16#FB44 = 64324 |  | = | CNL | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 1211
DRCF | Ref Freq Channel | 16#FB45 = 64325 |  | = | CNL | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 1212
DCC9 | Command Channel | 16#FB4A = 64330 |  | = | CNL | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 1213
DCCA | Command Channel | 16#FB4B = 64331 |  | = | CNL | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 1214
DCCB | Command Channel | 16#FB4C = 64332 |  | = | CNL | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 1215
DCCZ | Command Channel | 16#FB4D = 64333 |  | = | CNL | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 1216
DCCD | Command Channel | 16#FB4E = 64334 |  | = | CNL | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 1217
DCCE | Command Channel | 16#FB4F = 64335 |  | = | CNL | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 1218
DCCF | Command Channel | 16#FB50 = 64336 |  | = | CNL | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 1219
PFWU | Pipe Fill on Wake Up | 16#3DBE = 15806 | 16#2080/7 | 16#B0/01/07 = 176/01/07 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [Yes] (YES) | - | [Pipe Fill on Wake Up] (PFWU) | [Pipe fill] (PFI-) | 1220
SLPL | Sleep Pressure Level | 16#2DF2 = 11762 | 16#2057/3F | 16#9B/01/A3 = 155/01/163 | - | Configuration and settings | R/W | INT (Signed16) | (call PressureUnitSelected [SUPR]) | [No] (nO) | [No] (nO) ... (call PressureUnitSelected [SUPR]) | [Sleep Pressure Level] (SLPL) | [Settings] (SEt-) [Sleep menu] (SLP-) | 1221
WUPL | Wake Up Press level | 16#2DF3 = 11763 | 16#2057/40 | 16#9B/01/A4 = 155/01/164 | - | Configuration and settings | R/W | INT (Signed16) | (call PressureUnitSelected [SUPR]) | (call PressureUnitSelected [SUPR]) | (call PressureUnitSelected [SUPR]) ... (call PressureUnitSelected [SUPR]) | [Wake Up Press level] (WUPL) | [Settings] (SEt-) [Wake up menu] (W P-) | 1222
ILCI | Cabinet Input physical state | 16#1453 = 5203 | 16#2016/4 | 16#7B/01/04 = 123/01/04 | ILCI | I/O parameters | R | WORD (BitString16) | - |  | - |  |  | 1223
ILCR |  | 16#1454 = 5204 | 16#2016/5 | 16#7B/01/05 = 123/01/05 | ILCR | I/O parameters | R | WORD (BitString16) | - |  | - |  |  | 1224
OLCI | Cabinet Ouput physical state | 16#145D = 5213 | 16#2016/E | 16#7B/01/0E = 123/01/14 | OLCI | I/O parameters | R | WORD (BitString16) | - |  | - |  |  | 1225
OLCR |  | 16#145E = 5214 | 16#2016/F | 16#7B/01/0F = 123/01/15 | OLCR | I/O parameters | R/W | WORD (BitString16) | - |  | - |  |  | 1226
PSS | Pre-settings Status | 16#1F7C = 8060 | 16#2032/3D | 16#89/01/3D = 137/01/61 | PSS | Configuration management | R | WORD (Enumeration) | - |  | - | [Pre-settings Status] (PSS) | [Pre-settings] (PrES-) | 1227
CBS | CB status | 16#352B = 13611 | 16#206A/C | 16#A5/01/0C = 165/01/12 | CBS | Status parameters | [always] | WORD (Enumeration) | - | [CB Not Configured] (nO) | - | [CB status] (CbS) | [Circuit breaker] (CCb -) | 1228
BPI0 | Power Brick Error ID | 16#1E78 = 7800 | 16#2030/1 | 16#88/01/01 = 136/01/01 | BPI0 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 1229
BPI1 | Power Brick Error ID | 16#1E79 = 7801 | 16#2030/2 | 16#88/01/02 = 136/01/02 | BPI1 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 1230
BPI2 | Power Brick Error ID | 16#1E7A = 7802 | 16#2030/3 | 16#88/01/03 = 136/01/03 | BPI2 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 1231
BPI3 | Power Brick Error ID | 16#1E7B = 7803 | 16#2030/4 | 16#88/01/04 = 136/01/04 | BPI3 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 1232
BPI4 | Power Brick Error ID | 16#1E7C = 7804 | 16#2030/5 | 16#88/01/05 = 136/01/05 | BPI4 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 1233
BPI5 | Power Brick Error ID | 16#1E7D = 7805 | 16#2030/6 | 16#88/01/06 = 136/01/06 | BPI5 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 1234
BPI6 | Power Brick Error ID | 16#1E7E = 7806 | 16#2030/7 | 16#88/01/07 = 136/01/07 | BPI6 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 1235
BPI7 | Power Brick Error ID | 16#1E7F = 7807 | 16#2030/8 | 16#88/01/08 = 136/01/08 | BPI7 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 1236
BPI8 | Power Brick Error ID | 16#1E80 = 7808 | 16#2030/9 | 16#88/01/09 = 136/01/09 | BPI8 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 1237
BPI9 | Power Brick Error ID | 16#1E81 = 7809 | 16#2030/A | 16#88/01/0A = 136/01/10 | BPI9 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 1238
BPIA | Power Brick Error ID | 16#1E82 = 7810 | 16#2030/B | 16#88/01/0B = 136/01/11 | BPIA | History parameters | R | WORD (BitString16) | - |  | - |  |  | 1239
BPIB | Power Brick Error ID | 16#1E83 = 7811 | 16#2030/C | 16#88/01/0C = 136/01/12 | BPIB | History parameters | R | WORD (BitString16) | - |  | - |  |  | 1240
BPIC | Power Brick Error ID | 16#1E84 = 7812 | 16#2030/D | 16#88/01/0D = 136/01/13 | BPIC | History parameters | R | WORD (BitString16) | - |  | - |  |  | 1241
BPID | Power Brick Error ID | 16#1E85 = 7813 | 16#2030/E | 16#88/01/0E = 136/01/14 | BPID | History parameters | R | WORD (BitString16) | - |  | - |  |  | 1242
BPIE | Power Brick Error ID | 16#1E86 = 7814 | 16#2030/F | 16#88/01/0F = 136/01/15 | BPIE | History parameters | R | WORD (BitString16) | - |  | - |  |  | 1243
BPIF | Power Brick Error ID | 16#1E87 = 7815 | 16#2030/10 | 16#88/01/10 = 136/01/16 | BPIF | History parameters | R | WORD (BitString16) | - |  | - |  |  | 1244
BFI0 | AFE Power brick error ID | 16#1E8C = 7820 | 16#2030/15 | 16#88/01/15 = 136/01/21 | BFI0 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 1245
BFI1 | AFE Power brick error ID | 16#1E8D = 7821 | 16#2030/16 | 16#88/01/16 = 136/01/22 | BFI1 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 1246
BFI2 | AFE Power brick error ID | 16#1E8E = 7822 | 16#2030/17 | 16#88/01/17 = 136/01/23 | BFI2 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 1247
BFI3 | AFE Power brick error ID | 16#1E8F = 7823 | 16#2030/18 | 16#88/01/18 = 136/01/24 | BFI3 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 1248
BFI4 | AFE Power brick error ID | 16#1E90 = 7824 | 16#2030/19 | 16#88/01/19 = 136/01/25 | BFI4 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 1249
BFI5 | AFE Power brick error ID | 16#1E91 = 7825 | 16#2030/1A | 16#88/01/1A = 136/01/26 | BFI5 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 1250
BFI6 | AFE Power brick error ID | 16#1E92 = 7826 | 16#2030/1B | 16#88/01/1B = 136/01/27 | BFI6 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 1251
BFI7 | AFE Power brick error ID | 16#1E93 = 7827 | 16#2030/1C | 16#88/01/1C = 136/01/28 | BFI7 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 1252
BFI8 | AFE Power brick error ID | 16#1E94 = 7828 | 16#2030/1D | 16#88/01/1D = 136/01/29 | BFI8 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 1253
BFI9 | AFE Power brick error ID | 16#1E95 = 7829 | 16#2030/1E | 16#88/01/1E = 136/01/30 | BFI9 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 1254
BFIA | AFE Power brick error ID | 16#1E96 = 7830 | 16#2030/1F | 16#88/01/1F = 136/01/31 | BFIA | History parameters | R | WORD (BitString16) | - |  | - |  |  | 1255
BFIB | AFE Power brick error ID | 16#1E97 = 7831 | 16#2030/20 | 16#88/01/20 = 136/01/32 | BFIB | History parameters | R | WORD (BitString16) | - |  | - |  |  | 1256
BFIC | AFE Power brick error ID | 16#1E98 = 7832 | 16#2030/21 | 16#88/01/21 = 136/01/33 | BFIC | History parameters | R | WORD (BitString16) | - |  | - |  |  | 1257
BFID | AFE Power brick error ID | 16#1E99 = 7833 | 16#2030/22 | 16#88/01/22 = 136/01/34 | BFID | History parameters | R | WORD (BitString16) | - |  | - |  |  | 1258
BFIE | AFE Power brick error ID | 16#1E9A = 7834 | 16#2030/23 | 16#88/01/23 = 136/01/35 | BFIE | History parameters | R | WORD (BitString16) | - |  | - |  |  | 1259
BFIF | AFE Power brick error ID | 16#1E9B = 7835 | 16#2030/24 | 16#88/01/24 = 136/01/36 | BFIF | History parameters | R | WORD (BitString16) | - |  | - |  |  | 1260
ILN | Mains Current | 16#35D7 = 13783 | 16#206B/54 | 16#A5/01/B8 = 165/01/184 | - | Measurement parameters | R | UINT (Unsigned16) | Refer to programming manual |  | Depends of rating | [Mains Current] (ILn) | [Drive parameters] (MPI-) | 1261
IQRW | Input Reactive Power | 16#0CE2 = 3298 | 16#2002/63 | 16#71/01/63 = 113/01/99 | - | Actual values parameters | R | INT (Signed16) | Refer to programming manual |  | Depends of rating | [Input Reactive Power] (IqrW) | [Elec Ener Input Counter] (ELI-) | 1262
PWF | Input Power Factor | 16#35DA = 13786 | 16#206B/57 | 16#A5/01/BB = 165/01/187 | - | Actual values parameters | R | INT (Signed16) | 0.1 % |  | -32767 ... 32767 | [Input Power Factor] (PWF) | [Elec Ener Input Counter] (ELI-) | 1263
FAC | Mains Frequency | 16#35B6 = 13750 | 16#206B/33 | 16#A5/01/97 = 165/01/151 | - | Measurement parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz |  |  | 1264
FSBA |  | 16#35CA = 13770 | 16#206B/47 | 16#A5/01/AB = 165/01/171 | - | Measurement parameters | R | UINT (Unsigned16) | 1 rpm |  | 0 rpm ... 65535 rpm |  |  | 1265
FBAT | AFE Fan Operation Time | 16#35CB = 13771 | 16#206B/48 | 16#A5/01/AC = 165/01/172 |  | Actual values parameters | R | UINT (Unsigned32) | - |  | - | [AFE Fan Operation Time] (FbAt) | [Counter Management] (ELt-) | 1266
FCT | Cabinet Fan Oper Time | 16#35CD = 13773 | 16#206B/4A | 16#A5/01/AE = 165/01/174 |  | Actual values parameters | R/WS | UINT (Unsigned32) | - |  | - | [Cabinet Fan Oper Time] (FCt) | [Counter Management] (ELt-) | 1267
THDA |  | 16#9B22 = 39714 |  | = | - | Measurement parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 200 % |  |  | 1268
BRTH | AFE Run Time | 16#35CF = 13775 | 16#206B/4C | 16#A5/01/B0 = 165/01/176 |  | Actual values parameters | R | UINT (Unsigned32) | - |  | - | [AFE Run Time] (brtH) | [Counter Management] (ELt-) | 1269
BPTH | AFE Power-On Time | 16#35D1 = 13777 | 16#206B/4E | 16#A5/01/B2 = 165/01/178 |  | Actual values parameters | R | UINT (Unsigned32) | - |  | - | [AFE Power-On Time] (bPtH) | [Counter Management] (ELt-) | 1270
BNSA | AFE Nb of starts | 16#35D3 = 13779 | 16#206B/50 | 16#A5/01/B4 = 165/01/180 |  | Actual values parameters | R | UINT (Unsigned32) | - |  | - | [AFE Nb of starts] (bnSA) | [Counter Management] (ELt-) | 1271
CLIG | AFE Generator Mode | 16#35D9 = 13785 | 16#206B/56 | 16#A5/01/BA = 165/01/186 | - | Configuration and settings | R/W | INT (Signed16) | 0.1 % | [Low Harmonic] (LHM) | [Low Harmonic & Regen] (LHrM) ... 120.0 % | [AFE Generator Mode] (CLIG) | [Active Front End] (AFE-) [Settings] (SEt-) | 1272
SPD1 | Signed Mech Speed | 16#2EEC = 12012 | 16#205A/D | 16#9D/01/0D = 157/01/13 | RFQ | Actual values parameters | R | INT (Signed32) | - |  | - | [Signed Mech Speed] (SPd1) | [Motor parameters] (MMO-) | 1273
FDR0 | FDR Error Status | 16#FBB0 = 64432 |  | = | EFDR | Configuration management | R | WORD (Enumeration) | - |  | - | [FDR Error Status] (Fdr0) | [Fast Device Replacement] (Fdr-) | 1274
FDS0 | FDR Operating State | 16#FBB1 = 64433 |  | = | SFDR | Configuration management | R | WORD (Enumeration) | - |  | - | [FDR Operating State] (FdS0) | [Fast Device Replacement] (Fdr-) | 1275
FDA0 | FDR Action | 16#FBB2 = 64434 |  | = | FDRA | Configuration management | R/W | WORD (Enumeration) | - | [NOT ACTIVE] (IdLE) | - | [FDR Action] (FdA0) | [Fast Device Replacement] (Fdr-) | 1276
FDV0 | Enable FDR | 16#FBB3 = 64435 |  | = | N_Y | Configuration management | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Enable FDR] (FdU0) | [Fast Device Replacement] (Fdr-) | 1277
INF6 | Identification Error (INF6) | 16#1BE1 = 7137 | 16#2029/26 | 16#84/01/8A = 132/01/138 | - | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Identification Error (INF6)] (InF6) | [Diag. data] (ddt-) | 1278
HS1 | Drive state | 16#1C99 = 7321 | 16#202B/16 | 16#85/01/7A = 133/01/122 | HMIS | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 1279
HS2 | Drive state | 16#1C9A = 7322 | 16#202B/17 | 16#85/01/7B = 133/01/123 | HMIS | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 1280
HS3 | Drive state | 16#1C9B = 7323 | 16#202B/18 | 16#85/01/7C = 133/01/124 | HMIS | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 1281
HS4 | Drive state | 16#1C9C = 7324 | 16#202B/19 | 16#85/01/7D = 133/01/125 | HMIS | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 1282
HS5 | Drive state | 16#1C9D = 7325 | 16#202B/1A | 16#85/01/7E = 133/01/126 | HMIS | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 1283
HS6 | Drive state | 16#1C9E = 7326 | 16#202B/1B | 16#85/01/7F = 133/01/127 | HMIS | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 1284
HS7 | Drive state | 16#1C9F = 7327 | 16#202B/1C | 16#85/01/80 = 133/01/128 | HMIS | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 1285
HS8 | Drive state | 16#1CA0 = 7328 | 16#202B/1D | 16#85/01/81 = 133/01/129 | HMIS | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 1286
OTQN | Motor Torque (Nm) | 16#0CC4 = 3268 | 16#2002/45 | 16#71/01/45 = 113/01/69 | - | Actual values parameters | R | INT (Signed16) | Refer to programming manual |  | Depends of rating | [Motor Torque (Nm)] (Otqn) | [Motor parameters] (MMO-) [Display] (SUP-) | 1287
TQN | Nom Motor torque | 16#25C5 = 9669 | 16#2042/46 | 16#91/01/46 = 145/01/70 | - | Actual values parameters | [always] | UINT (Unsigned16) | Refer to programming manual | Depends of rating | Depends of rating | [Nom Motor torque] (tqn) | [Motor parameters] (MMO-) | 1288
UL1 | Mains voltage phase 1-2 | 16#35B3 = 13747 | 16#206B/30 | 16#A5/01/94 = 165/01/148 | - | Measurement parameters | R | INT (Signed16) | 0.1 V |  | -3276.7 V ... 3276.7 V | [Mains voltage phase 1-2] (UL1) | [Drive parameters] (MPI-) | 1289
UL2 | Mains voltage phase 2-3 | 16#35B4 = 13748 | 16#206B/31 | 16#A5/01/95 = 165/01/149 | - | Measurement parameters | R | INT (Signed16) | 0.1 V |  | -3276.7 V ... 3276.7 V | [Mains voltage phase 2-3] (UL2) | [Drive parameters] (MPI-) | 1290
UL3 | Mains voltage phase 3-1 | 16#35B5 = 13749 | 16#206B/32 | 16#A5/01/96 = 165/01/150 | - | Measurement parameters | R | INT (Signed16) | 0.1 V |  | -3276.7 V ... 3276.7 V | [Mains voltage phase 3-1] (UL3) | [Drive parameters] (MPI-) | 1291
APPT | Application Selection | 16#3D53 = 15699 | 16#207E/64 | 16#AF/01/64 = 175/01/100 | APPT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Generic Pump Control] (GPMP) | - | [Application Selection] (APPt) | [Macro Configuration] (MCr-) | 1292
MPC | Motor param choice | 16#258E = 9614 | 16#2042/F | 16#91/01/0F = 145/01/15 | MPC | Configuration and settings | R/WS | WORD (Enumeration) | - | [Mot Power] (nPr) | - | [Motor param choice] (MPC) | [data] (Mtd-) | 1293
CRFA | Currents Filter | 16#239E = 9118 | 16#203D/13 | 16#8E/01/77 = 142/01/119 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 ms |  | 0.0 ms ... 100.0 ms | [Currents Filter] (CrFA) | [data] (Mtd-) | 1294
RDAE | % error EMF sync | 16#25CC = 9676 | 16#2042/4D | 16#91/01/4D = 145/01/77 | - | Actual values parameters | R | INT (Signed16) | 0.1 % |  | 0.0 % ... 6553.5 % | [% error EMF sync] (rdAE) | [data] (Mtd-) | 1295
TUNU | Autotuning Usage | 16#2593 = 9619 | 16#2042/14 | 16#91/01/14 = 145/01/20 | TUNU | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Autotuning Usage] (tUnU) | [Motor tune] (MtU-) | 1296
TCR | Autotuning Lvl Of Current | 16#259B = 9627 | 16#2042/1C | 16#91/01/1C = 145/01/28 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | [Auto] (AUtO) | [Auto] (AUtO) ... 300 % | [Autotuning Lvl Of Current] (tCr) | [Motor tune] (MtU-) | 1297
RCL | Rotational Current Level | 16#3668 = 13928 | 16#206D/1D | 16#A6/01/81 = 166/01/129 | - | Configuration and settings | R/WS | INT (Signed16) | 1 % | 75 % | 10 % ... 300 % | [Rotational Current Level] (rCL) | [Motor tune] (MtU-) | 1298
RCIR | RCI With Transformer | 16#366A = 13930 | 16#206D/1F | 16#A6/01/83 = 166/01/131 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [RCI With Transformer] (rCIr) | [Motor tune] (MtU-) | 1299
RCSP | RCI Max Freq | 16#366B = 13931 | 16#206D/20 | 16#A6/01/84 = 166/01/132 | - | Configuration and settings | R/WS | INT (Signed16) | 0.1 Hz | 0.0 Hz | [Auto] (AUtO) ... 500.0 Hz | [RCI Max Freq] (rCSP) | [Motor tune] (MtU-) | 1300
TH3V | AI3 Th Value | 16#33C3 = 13251 | 16#2066/34 | 16#A3/01/34 = 163/01/52 | - | Measurement parameters | R | INT (Signed16) | (call TemperatureUnitSelection [SUTP]) |  | (call TemperatureUnitSelection [SUTP]) ... (call TemperatureUnitSelection [SUTP]) | [AI3 Th Value] (tH3U) | [Thermal Monitoring] (tPM-) [Thermal monitoring] (tPP-) [Display] (SUP-) | 1301
TH4V | AI4 Th Value | 16#33C4 = 13252 | 16#2066/35 | 16#A3/01/35 = 163/01/53 | - | Measurement parameters | R | INT (Signed16) | (call TemperatureUnitSelection [SUTP]) |  | (call TemperatureUnitSelection [SUTP]) ... (call TemperatureUnitSelection [SUTP]) | [AI4 Th Value] (tH4U) | [Thermal Monitoring] (tPM-) [Thermal monitoring] (tPP-) [Display] (SUP-) | 1302
TH5V | AI5 Th Value | 16#33C5 = 13253 | 16#2066/36 | 16#A3/01/36 = 163/01/54 | - | Measurement parameters | R | INT (Signed16) | (call TemperatureUnitSelection [SUTP]) |  | (call TemperatureUnitSelection [SUTP]) ... (call TemperatureUnitSelection [SUTP]) | [AI5 Th Value] (tH5U) | [Thermal Monitoring] (tPM-) [Thermal monitoring] (tPP-) [Display] (SUP-) | 1303
BOO | Boost | 16#3658 = 13912 | 16#206D/D | 16#A6/01/71 = 166/01/113 | - | Configuration and settings | R/WS | INT (Signed16) | 1 % | Refer to programming manual | -100 % ... 100 % | [Boost] (bOO) | [Motor control] (drC-) | 1304
FAB | Freq Boost | 16#3657 = 13911 | 16#206D/C | 16#A6/01/70 = 166/01/112 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0.0 Hz ... 500.0 Hz | [Freq Boost] (FAb) | [Motor control] (drC-) | 1305
MLTO | MDL Comm Timeout | 16#17C5 = 6085 | 16#201E/56 | 16#7F/01/56 = 127/01/86 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 s | 0.25 s | 0.05 s ... 10.00 s |  |  | 1306
TPMM | Pmax Motor | 16#2400 = 9216 | 16#203E/11 | 16#8F/01/11 = 143/01/17 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 300 % | 10 % ... 300 % | [Pmax Motor] (tPMM) | [Torque limitation] (tOL-) [Settings] (SEt-) | 1307
TPMG | Pmax Generator | 16#2401 = 9217 | 16#203E/12 | 16#8F/01/12 = 143/01/18 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 300 % | 10 % ... 300 % | [Pmax Generator] (tPMG) | [Torque limitation] (tOL-) [Settings] (SEt-) | 1308
TWO | Term word order | 16#1776 = 6006 | 16#201E/7 | 16#7F/01/07 = 127/01/07 | TWO | Configuration and settings | R/WS | WORD (Enumeration) | - | [ON] (HIGH) | - | [Term word order] (tWO) | [Modbus Fieldbus] (Md1-) | 1309
TWO2 | Term 2 word order | 16#178A = 6026 | 16#201E/1B | 16#7F/01/1B = 127/01/27 | TWO | Configuration and settings | R/WS | WORD (Enumeration) | - | [ON] (HIGH) | - | [Term 2 word order] (tWO2) | [Modbus HMI] (Md2-) | 1310
AV2J | AIV2 Lowest Process | 16#11AB = 4523 | 16#200F/18 | 16#77/01/7C = 119/01/124 | - | Configuration and settings | R/WS | INT (Signed16) | 1 | 0 | -32767 ... 32767 | [AIV2 Lowest Process] (AU2J) | [AIV2 Sensor Config.] (ICU2-) [AIV2 Sensor Config.] (OCU2-) [AIV2 Sensor Config.] (IFU2-) [AIV2 Sensor Config.] (HIU2-) [AIV2 Sensor Config.] (FIU2-) [AIV2 Sensor Config.] (LFU2-) [AIV2 Sensor Config.] (bIU2-) [AIV2 Configuration] (LIU2-) [AIV2 Configuration] (PFU2-) [AIV2 Sensor Config.] (nPU2-) [AIV2 Sensor Config.] (IPU2-) [AIV2 Sensor Config.] (PPU2-) [AIV2 Sensor Config.] (OOU2-) [AIV2 Configuration] (LCU2-) [AIV2 Sensor Config.] (LSU2-) [AIV2 Sensor Config.] (SIU2-) [AIV2 Sensor Config.] (SOU2-) [AIV2 Sensor Config.] (WOU2-) [AIV2 Sensor Config.] (PF2U-) | 1311
AV2K | AIV2 Highest Process | 16#11B5 = 4533 | 16#200F/22 | 16#77/01/86 = 119/01/134 | - | Configuration and settings | R/WS | INT (Signed16) | 1 | 0 | -32767 ... 32767 | [AIV2 Highest Process] (AU2 ) | [AIV2 Sensor Config.] (ICU2-) [AIV2 Sensor Config.] (OCU2-) [AIV2 Sensor Config.] (IFU2-) [AIV2 Sensor Config.] (HIU2-) [AIV2 Sensor Config.] (FIU2-) [AIV2 Sensor Config.] (LFU2-) [AIV2 Sensor Config.] (bIU2-) [AIV2 Configuration] (LIU2-) [AIV2 Configuration] (PFU2-) [AIV2 Sensor Config.] (nPU2-) [AIV2 Sensor Config.] (IPU2-) [AIV2 Sensor Config.] (PPU2-) [AIV2 Sensor Config.] (OOU2-) [AIV2 Configuration] (LCU2-) [AIV2 Sensor Config.] (LSU2-) [AIV2 Sensor Config.] (SIU2-) [AIV2 Sensor Config.] (SOU2-) [AIV2 Sensor Config.] (WOU2-) [AIV2 Sensor Config.] (PF2U-) | 1312
AIV2 | AIV2 Image input | 16#14A3 = 5283 | 16#2016/54 | 16#7B/01/54 = 123/01/84 | - | Setpoint parameters | [always] | INT (Signed16) | 1 | 0 | -8192 ... 8192 | [AIV2 Image input] (AIU2) | [Drive parameters] (MPI-) | 1313
AIC2 | AI2 net. Channel | 16#14A4 = 5284 | 16#2016/55 | 16#7B/01/55 = 123/01/85 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Configured] (nO) | - | [AI2 net. Channel] (AIC2) | [Virtual AI2] (AU2-) | 1314
AV3J | AIV3 Lowest Process | 16#11AC = 4524 | 16#200F/19 | 16#77/01/7D = 119/01/125 | - | Configuration and settings | R/WS | INT (Signed16) | 1 | 0 | -32767 ... 32767 | [AIV3 Lowest Process] (AU3J) | [AIV3 Sensor Config.] (ICU3-) [AIV3 Sensor Config.] (OCU3-) [AIV3 Sensor Config.] (IFU3-) [AIV3 Sensor Config.] (HIU3-) [AIV3 Sensor Config.] (FIU3-) [AIV3 Sensor Config.] (LFU3-) [AIV3 Sensor Config.] (bIU3-) [AIV3 Configuration] (LIU3-) [AIV3 Configuration] (PFU3-) [AIV3 Sensor Config.] (nPU3-) [AIV3 Sensor Config.] (IPU3-) [AIV3 Sensor Config.] (PPU3-) [AIV3 Sensor Config.] (OOU3-) [AIV3 Configuration] (LCU3-) [AIV3 Sensor Config.] (LSU3-) [AIV3 Sensor Config.] (SIU3-) [AIV3 Sensor Config.] (SOU3-) [AIV3 Sensor Config.] (WOU3-) [AIV3 Sensor Config.] (PF3U-) | 1315
AV3K | AIV3 Highest Process | 16#11B6 = 4534 | 16#200F/23 | 16#77/01/87 = 119/01/135 | - | Configuration and settings | R/WS | INT (Signed16) | 1 | 0 | -32767 ... 32767 | [AIV3 Highest Process] (AU3 ) | [AIV3 Sensor Config.] (ICU3-) [AIV3 Sensor Config.] (OCU3-) [AIV3 Sensor Config.] (IFU3-) [AIV3 Sensor Config.] (HIU3-) [AIV3 Sensor Config.] (FIU3-) [AIV3 Sensor Config.] (LFU3-) [AIV3 Sensor Config.] (bIU3-) [AIV3 Configuration] (LIU3-) [AIV3 Configuration] (PFU3-) [AIV3 Sensor Config.] (nPU3-) [AIV3 Sensor Config.] (IPU3-) [AIV3 Sensor Config.] (PPU3-) [AIV3 Sensor Config.] (OOU3-) [AIV3 Configuration] (LCU3-) [AIV3 Sensor Config.] (LSU3-) [AIV3 Sensor Config.] (SIU3-) [AIV3 Sensor Config.] (SOU3-) [AIV3 Sensor Config.] (WOU3-) [AIV3 Sensor Config.] (PF3U-) | 1316
AIV3 | AIV3 Image input | 16#14A5 = 5285 | 16#2016/56 | 16#7B/01/56 = 123/01/86 | - | Setpoint parameters | [always] | INT (Signed16) | 1 | 0 | -8192 ... 8192 | [AIV3 Image input] (AIU3) | [Drive parameters] (MPI-) | 1317
AIC3 | AIV3 Channel Assign | 16#14A6 = 5286 | 16#2016/57 | 16#7B/01/57 = 123/01/87 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Configured] (nO) | - | [AIV3 Channel Assign] (AIC3) | [Virtual AI3] (AU3-) | 1318
SLFS | Sys Flow | 16#3E95 = 16021 | 16#2082/16 | 16#B1/01/16 = 177/01/22 | - | Actual values parameters | R | INT (Signed16) | (call FlowRateUnitSelection [SUFR]) |  | (call FlowRateUnitSelection [SUFR]) ... (call FlowRateUnitSelection [SUFR]) | [Sys Flow] (SLFS) | [Installation] (MPUS-) | 1319
EPRS | Sys Electrical Power | 16#3E97 = 16023 | 16#2082/18 | 16#B1/01/18 = 177/01/24 | - | Actual values parameters | R | INT (Signed16) | Refer to programming manual |  | Depends of rating | [Sys Electrical Power] (EPrS) | [Installation] (MPUS-) | 1320
EFYS | Sys Efficiency Ind | 16#3E98 = 16024 | 16#2082/19 | 16#B1/01/19 = 177/01/25 | - | Actual values parameters | R | INT (Signed16) | 0.1 % |  | 0.0 % ... 100.0 % | [Sys Efficiency Ind] (EFYS) | [Installation] (MPUS-) | 1321
ECIS | Sys Energy Cons Ind | 16#3E99 = 16025 | 16#2082/1A | 16#B1/01/1A = 177/01/26 | - | Actual values parameters | R | INT (Signed16) | (call WaterSpecificEnergyUnitSelection [SUFR]) |  | (call WaterSpecificEnergyUnitSelection [SUFR]) ... (call WaterSpecificEnergyUnitSelection [SUFR]) | [Sys Energy Cons Ind] (ECIS) | [Installation] (MPUS-) | 1322
EPIS | Sys Performance Ind | 16#3E9A = 16026 | 16#2082/1B | 16#B1/01/1B = 177/01/27 | - | Actual values parameters | R | INT (Signed16) | (call NRGPerformanceUnitSelection [SUFR]) |  | (call NRGPerformanceUnitSelection [SUFR]) ... (call NRGPerformanceUnitSelection [SUFR]) | [Sys Performance Ind] (EPIS) | [Installation] (MPUS-) | 1323
MPGN | Nb of Devices | 16#4075 = 16501 | 16#2087/2 | 16#B3/01/66 = 179/01/102 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 1 | 0 ... 6 | [Nb of Devices] (MPGn) | [System Architecture] (MPq-) | 1324
MGID | M/P Device ID | 16#4076 = 16502 | 16#2087/3 | 16#B3/01/67 = 179/01/103 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | [No] (nO) | [No] (nO) ... 6 | [M/P Device ID] (MGId) | [System Architecture] (MPq-) | 1325
MPST | M/P Speed Mode | 16#4078 = 16504 | 16#2087/5 | 16#B3/01/69 = 179/01/105 | MPST | Configuration and settings | R/WS | WORD (Enumeration) | - | [Standard] (tMC) | - | [M/P Speed Mode] (MPSt) | [Booster Control] (bSC-) | 1326
MDLB | MultiDrive ErrorResp | 16#40CC = 16588 | 16#2087/59 | 16#B3/01/BD = 179/01/189 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel Stop] (YES) | - | [MultiDrive ErrorResp] (MdLb) | [System Architecture] (MPq-) | 1327
MPDB | M/P Device ErrorResp | 16#40CD = 16589 | 16#2087/5A | 16#B3/01/BE = 179/01/190 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel Stop] (YES) | - | [M/P Device ErrorResp] (MPdb) | [System Architecture] (MPq-) | 1328
MPDT | M/P Device Role | 16#40D5 = 16597 | 16#2087/62 | 16#B3/01/C6 = 179/01/198 | MPDT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Slave] (SLAUE) | - | [M/P Device Role] (MPdt) | [System Architecture] (MPq-) | 1329
MPFS | Pump Fixed Freq | 16#40D6 = 16598 | 16#2087/63 | 16#B3/01/C7 = 179/01/199 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0.0 Hz ... 500.0 Hz | [Pump Fixed Freq] (MPFS) | [Settings] (SEt-) [Booster Control] (bSC-) | 1330
BSDH | Booster S/D Flow Hyst | 16#40F5 = 16629 | 16#2088/1E | 16#B4/01/1E = 180/01/30 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 % | 3.0 % | 0.0 % ... 100.0 % | [Booster S/D Flow Hyst] (bSdH) | [Settings] (SEt-) [Stage/Destage Condition] (SdCM-) | 1331
LCPN | LevelCtrl Nb Of Pumps | 16#410A = 16650 | 16#2088/33 | 16#B4/01/33 = 180/01/51 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 6 | [LevelCtrl Nb Of Pumps] (LCPn) | [Level Control] (LCC-) | 1332
LCDK | Max Delivery Height | 16#4130 = 16688 | 16#2088/59 | 16#B4/01/59 = 180/01/89 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 m | [No] (nO) | [No] (nO) ... 327.67 m | [Max Delivery Height] (LCd ) | [Settings] (SEt-) [Level Control] (LCC-) | 1333
LCDJ | Min Delivery Height | 16#412F = 16687 | 16#2088/58 | 16#B4/01/58 = 180/01/88 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 m | [No] (nO) | [No] (nO) ... 327.67 m | [Min Delivery Height] (LCdJ) | [Settings] (SEt-) [Level Control] (LCC-) | 1334
LCQG | Disturb Flow Comp | 16#4133 = 16691 | 16#2088/5C | 16#B4/01/5C = 180/01/92 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 % | 100.0 % | 0.0 % ... 200.0 % | [Disturb Flow Comp] (LCqG) | [Level Control] (LCC-) | 1335
LCDT | LevelCtrl S/D Interval | 16#4138 = 16696 | 16#2088/61 | 16#B4/01/61 = 180/01/97 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 15.0 s | 0.0 s ... 999.9 s | [LevelCtrl S/D Interval] (LCdt) | [Settings] (SEt-) [Level Control] (LCC-) | 1336
FDR1 | FDR Error Status | 16#FBBA = 64442 |  | = | EFDR | Configuration and settings | R | WORD (Enumeration) | - |  | - | [FDR Error Status] (Fdr1) | [Fast Device Replacement] (FdrO-) | 1337
FDS1 | FDR Operating State | 16#FBBB = 64443 |  | = | SFDR | Configuration and settings | R | WORD (Enumeration) | - |  | - | [FDR Operating State] (FdS1) | [Fast Device Replacement] (FdrO-) | 1338
FDA1 | FDR Action | 16#FBBC = 64444 |  | = | FDRA | Configuration and settings | R/W | WORD (Enumeration) | - | [NOT ACTIVE] (IdLE) | - | [FDR Action] (FdA1) | [Fast Device Replacement] (FdrO-) | 1339
FDV1 | Enable FDR | 16#FBBD = 64445 |  | = | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Enable FDR] (FdU1) | [Fast Device Replacement] (FdrO-) | 1340
CIC2 |  | 16#1C16 = 7190 | 16#2029/5B | 16#84/01/BF = 132/01/191 | CIC2 | Fault parameters | R/WS | WORD (BitString16) | - |  | - |  |  | 1341
ST20 |  | 16#3EF8 = 16120 | 16#2083/15 | 16#B1/01/79 = 177/01/121 | ST20 | Status parameters | R | WORD (BitString16) | - |  | - |  |  | 1342

## Enumerations
Code | Values | Display | Description
ACT | 0 | [Not Done] (tAb)
| 1 | [Pending] (PEnd)
| 2 | [In Progress] (PrOG)
| 3 | [Error] (FAIL)
| 4 | [Autotuning Done] (dOnE)
ACTION | 0 | [No action] (nO)
| 1 | [Apply Autotuning] (YES)
| 2 | [Erase Autotuning] (CLr)
ADC | 0 | [No] (nO)
| 1 | [Yes] (YES)
| 2 | [Continuous] (Ct)
AIOT | 1 | [Voltage] (10U)
| 2 | [Current] (0A)
| 5 | [Voltage +/-] (n10U)
| 7 | [PTC MANAGEMENT] (PtC)
| 8 | [KTY] ( tY)
| 9 | [PT1000] (1Pt3)
| 10 | [PT100] (1Pt2)
| 11 | [Water Prob] (LEUEL)
| 12 | [3 PT1000] (3Pt3)
| 13 | [3 PT100] (3Pt2)
| 14 | [PT1000 in 3 wires] (1Pt33)
| 15 | [PT100 in 3 wires] (1Pt23)
| 16 | [3 PT1000 in 3 wires] (3Pt33)
| 17 | [3 PT100 in 3 wires] (3Pt23)
ALR | 0 | [No Warning stored] (nOA)
| 1 | [Fallback Frequency] (FrF)
| 2 | [Speed Maintained] (rLS)
| 3 | [Type of stop] (Stt)
| 4 | [Ref Frequency Warning] (SrA)
| 5 | [Life Cycle Warn 1] (LCA1)
| 6 | [Life Cycle Warn 2] (LCA2)
| 7 | [Drive Running Warning] (drYA)
| 8 | [Low Flow Warning] (LFA)
| 9 | [High Flow Warning] (HFPA)
| 10 | [InPress Warning] (IPPA)
| 11 | [Low OutPres Warning] (OPLA)
| 12 | [High OutPres Warning] (OPHA)
| 13 | [PumpCycle warning] (PCPA)
| 14 | [Anti-Jam Warning] (JAMA)
| 15 | [Pump Low Flow] (PLFA)
| 16 | [LowPres Warning] (LPA)
| 17 | [Flow Limit activated] (FSA)
| 18 | [PID error Warning] (PEE)
| 19 | [PID feedback Warning] (PFA)
| 20 | [PID High Fdbck Warning] (PFAH)
| 21 | [PID Low Fdbck Warning] (PFAL)
| 22 | [Regulation Warning] (PISH)
| 26 | [AI2 Th Warning] (tP2A)
| 27 | [AI3 Th Warning] (tP3A)
| 28 | [AI4 Th Warning] (tP4A)
| 29 | [AI5 Th Warning] (tP5A)
| 30 | [AI1 4-20 Loss Warning] (AP1)
| 31 | [AI2 4-20 Loss Warning] (AP2)
| 32 | [AI3 4-20 Loss Warning] (AP3)
| 33 | [AI4 4-20 Loss Warning] (AP4)
| 34 | [AI5 4-20 Loss Warning] (AP5)
| 35 | [Drive Thermal Warning] (tHA)
| 36 | [IGBT Thermal Warning] (tJA)
| 37 | [Fan Counter Warning] (FCtA)
| 38 | [Fan Feedback Warning] (FFdA)
| 40 | [Ext. Error Warning] (EFA)
| 41 | [Undervoltage Warning] (USA)
| 42 | [Preventive UnderV Active] (UPA)
| 44 | [Mot Freq High Thd] (FtA)
| 45 | [Mot Freq Low Thd] (FtAL)
| 47 | [Mot Freq Low Thd 2] (F2AL)
| 48 | [High Speed Reached] (FLA)
| 49 | [Ref Freq High Thd reached] (rtAH)
| 50 | [Ref Freq Low Thd reached] (rtAL)
| 51 | [2nd Freq Thd Reached] (F2A)
| 52 | [Current Thd Reached] (CtA)
| 53 | [Low Current Reached] (CtAL)
| 54 | [High Torque Warning] (ttHA)
| 55 | [Low Torque Warning] (ttLA)
| 56 | [Process Undld Warning] (ULA)
| 57 | [Process Overload Warning] (OLA)
| 60 | [Drv Therm Thd reached] (tAd)
| 61 | [Motor Therm Thd reached] (tSA)
| 65 | [Power High Threshold] (PtHA)
| 66 | [Power Low Threshold] (PtHL)
| 67 | [Cust Warning 1] (CAS1)
| 68 | [Cust Warning 2] (CAS2)
| 69 | [Cust Warning 3] (CAS3)
| 70 | [Cust Warning 4] (CAS4)
| 71 | [Cust Warning 5] (CAS5)
| 72 | [AFE Mains Undervoltage] (UrA)
| 73 | [Power Cons Warning] (POWd)
| 74 | [Switch OutPres Warning] (OPSA)
| 75 | [Ethernet Internal Warning] (InWM)
| 76 | [Auto Backup Not Plugged] (drAP)
| 77 | [Auto Backup Warning] (drtF)
| 78 | [MultiPump Capacity Warn] (MPCA)
| 79 | [Lead Pump Warn] (MPLA)
| 80 | [High Level Warning] (LCHA)
| 81 | [Low Level Warning] (LCLA)
| 82 | [Level Switch Warning] (LCWA)
| 97 | [MonitorCircuit A Warn] (IWA)
| 98 | [MonitorCircuit B Warn] (IWb)
| 99 | [MonitorCircuit C Warn] (IWC)
| 100 | [MonitorCircuit D Warn] (IWd)
| 101 | [CabinetCircuit A Warn] (CWA)
| 102 | [CabinetCircuit B Warn] (CWb)
| 103 | [CabinetCircuit C Warn] (CWC)
| 104 | [MotorWinding A Warn] (tWA)
| 105 | [MotorWinding B Warn] (tWb)
| 106 | [MotorBearing A Warn] (tWC)
| 107 | [MotorBearing B Warn] (tWd)
| 108 | [Circuit Breaker Warn] (CbW)
| 113 | [AFE Motor Limitation] (CLIM)
| 114 | [AFE Generator Limitation] (CLIG)
| 115 | [AFE Sensor thermal state] (tHSA)
| 116 | [AFE IGBT thermal state] (tHJA)
| 117 | [Cabinet Fan Fdbck Warn] (FFCA)
| 118 | [Cabinet Fan Counter Warn] (FCCA)
| 119 | [Cabinet Overheat Warn] (CHA)
| 120 | [CMI Jumper Warn] (CMIJ)
| 121 | [AFE Fan Counter Warn] (FCbA)
| 122 | [AFE Fan Fdbck Warn] (FFbA)
| 124 | [M/P Device Warn] (MPdA)
APPS | 0 | [Running] (rUn)
| 1 | [Stop] (StOP)
| 2 | [Local Mode Active] (LOCAL)
| 3 | [Channel 2 Active] (OUEr)
| 4 | [Manual Mode Active] (MAnU)
| 5 | [PID Active] (AUtO)
| 6 | [Anti-Jam In progress] (AJAM)
| 7 | [Flow limit In progress] (FLIM)
| 8 | [PipeFill In progress] (FILL)
| 9 | [Jockey Pump Active] (JOC EY)
| 10 | [Boost In progress] (bOOSt)
| 11 | [Sleep Active] (SLEEP)
| 12 | [Priming Pump Active] (PrIM)
| 13 | [InletPres Comp In progress] (COMP)
APPT | 0 | [Generic Pump Control] (GPMP)
| 1 | [Pump Level Control] (LEUEL)
| 2 | [Pump Booster Control] (bOOSt)
| 3 | [Generic Fan Control] (FAn)
AST | 5 | [PSI align.] (PSI)
| 6 | [PSIO align.] (PSIO)
| 7 | [Rotational Current Injection] (rCI)
| 254 | [No align.] (nO)
AUT | 0 | [No] (nO)
| 1 | [Yes] (YES)
BDCO | 38 | [50 kbps] (50 )
| 52 | [125 kbps] (125 )
| 60 | [250 kbps] (250 )
| 68 | [500 kbps] (500 )
| 76 | [1 Mbps] (1M)
BFR | 0 | [50Hz IEC] (50)
| 1 | [60Hz NEMA] (60)
BMP | 0 | [Stop] (StOP)
| 1 | [Bumpless] (bUMP)
| 2 | [Disabled] (dIS)
BOA | 0 | [Inactive] (nO)
| 1 | [Dynamic] (dYnA)
| 2 | [Static] (StAt)
| 3 | [Constant] (CStE)
BRA | 0 | [No] (nO)
| 1 | [Yes] (YES)
| 2 | [High Torque] (dYnA)
BSP | 0 | [Standard] (bSd)
| 1 | [Deadband] (bLS)
| 2 | [Pedestal] (bnS)
| 4 | [Pedestal at 0%] (bnS0)
CAR | 0 | [No Warning Clearing] (nO)
| 1 | [Clear Event 1 Warning] (rA1)
| 2 | [Clear Event 2 Warning] (rA2)
| 3 | [Clear Event 3 Warning] (rA3)
| 4 | [Clear Event 4 Warning] (rA4)
| 5 | [Clear Event 5 Warning] (rA5)
CBS | 0 | [CB Not Configured] (nO)
| 1 | [CB Invalid Config] (CbCI)
| 2 | [CB In Start Pulse] (CbSt)
| 3 | [CB Not Closed] (CbnC)
| 4 | [CB Open] (CbOS)
| 5 | [CB In Stop Pulse] (CbSP)
| 6 | [CB Not Open] (CbnO)
| 7 | [CB Closed] (CbCS)
| 8 | [CB stop disable] (CbSd)
CCA | 0 | [Not Configured] (nO)
| 1 | [Counter] (CPt)
| 2 | [Date and Time] (dt)
CCS | 0 | [Pwr/Control suppl ON] (0)
| 1 | [Supply Mains ON] (1)
| 2 | [Drv in run state] (2)
CDX | 1 | [Terminals] (tEr)
| 3 | [HMI] (LCC)
| 10 | [Modbus] (Mdb)
| 20 | [CANopen] (CAn)
| 30 | [Com. Module] (nEt)
| 40 | [Ethernet] (EtH)
CFPS | 0 | [None] (nO)
| 1 | [Set No.1] (CFP1)
| 2 | [Set No.2] (CFP2)
| 3 | [Set No.3] (CFP3)
CHCF | 1 | [Not separ.] (SIM)
| 2 | [Separate] (SEP)
| 3 | [I/O profile] (IO)
CINR | 20 | (0.001)
| 30 | (0.01)
| 40 | (0.1)
| 50 | (1)
| 60 | (10)
CIOA | 0 | [20/70] (20)
| 1 | [21/71] (21)
| 2 | [100/101] (100)
| 3 | [Unconfig.] (UnCG)
CNFS | 0 | [In progress] (nO)
| 1 | [Config. No.0] (CnF0)
CNL | 0 | [Terminals] (tErM)
| 2 | [HMI] (HMI)
| 3 | [Modbus] (Mdb)
| 6 | [CANopen] (CAn)
| 9 | [Com. Module] (nEt)
| 11 | [Ethernet Module] (EtH)
| 15 | [PC tool] (PWS)
COP | 0 | [No] (nO)
| 1 | [Reference Frequency] (SP)
| 2 | [Command] (Cd)
| 3 | [Cmd + Ref Frequency] (ALL)
CSLFN | 0 | [Not Assigned] (nO)
| 181 | [Preset Speed 1] (FPS1)
| 182 | [Preset Speed 2] (FPS2)
| 183 | [PID Ref Freq 1] (FPr1)
| 184 | [PID Ref Freq 2] (FPr2)
| 185 | [+speed] (FUSP)
| 186 | [-speed] (FdSP)
CSLOUT | 0 | [Not Assigned] (nO)
| 146 | [R2] (r2)
| 147 | [R3] (r3)
| 148 | [R4] (r4)
| 149 | [R5] (r5)
| 150 | [R6] (r6)
| 163 | [DQ11 Digital Output] (dO11)
| 164 | [DQ12 Digital Output] (dO12)
| 200 | [VSP] (USP)
| 209 | [R60] (r60)
| 210 | [R61] (r61)
| 211 | [R62] (r62)
| 212 | [R63] (r63)
| 213 | [R64] (r64)
| 214 | [R65] (r65)
| 215 | [R66] (r66)
CTT | 3 | [U/F VC Standard] (Std)
| 4 | [U/F VC 5pts] (UF5)
| 6 | [U/F VC Quad.] (UFq)
| 10 | [SYN_U VC] (SYnU)
| 11 | [U/F VC Energy Sav.] (ECO)
DOTD | 0 | [Freewheel stop] (nSt)
| 1 | [Ramp stop] (rMP)
DPMA | 1 | [MCL1] (1)
| 2 | [MCL2] (2)
DRT | 0 | [Normal Duty] (nOrMAL)
| 1 | [Heavy Duty] (HIGH)
DRYM | 0 | [No] (nO)
| 1 | [Switch] (SWt)
| 2 | [Power] (PWr)
DUR | 0 | [5 minutes] (5)
| 1 | [10 minutes] (10)
| 2 | [30 minutes] (30)
| 3 | [1 hour] (1H)
| 4 | [2 hours] (2H)
| 5 | [3 hours] (3H)
| 6 | [Unlimited] (Ct)
ECFG | 0 | [Ignore] (nO)
| 1 | [Freewheel Stop] (YES)
| 2 | [Per STT] (Stt)
| 4 | [Fallback Speed] (LFF)
| 5 | [Speed maintained] (rLS)
| 6 | [Ramp stop] (rMP)
| 7 | [Fast stop] (FSt)
| 8 | [DC injection] (dCI)
EFDR | 0 | [No Error] (nO)
| 1 | [Server Timeout] (tOUt)
| 2 | [Server No File] (SnF)
| 3 | [Server Corrupt File] (CrPt)
| 4 | [Server Empty File] (EPtY)
| 5 | [Drive Invalid File] (HInU)
| 6 | [CRC Error] (CrC)
| 7 | [Version Incompatibility] (UrM)
| 9 | [Drive No File] (HnF)
| 10 | [Server Reading Size] (SIZE)
| 11 | [Drive Opening File] (OPEn)
| 12 | [Drive Reading File] (rEAd)
| 13 | [Incompatibility] (SCnt)
| 14 | [Drive Invalid Name] (nInU)
| 15 | [Server Incorrect File Size] (FSIZ)
| 16 | [Drive Writing File] (HWF)
| 17 | [Server Writing File] (SWF)
ERRD | 16#0000 | [No Error] (nOF)
| 16#1000 | [Precharge Capacitor] (CrF)
| 16#1000 | [Motor Overspeed] (SOF)
| 16#1000 | [Internal Error 14] (InFE)
| 16#1000 | [Channel Switch Error] (CSF)
| 16#1000 | [Angle error] (ASF)
| 16#2130 | [AFE ShortCircuit error] (SCF6)
| 16#2230 | [IGBT Short Circuit] (SCF4)
| 16#2310 | [Overcurrent] (OCF)
| 16#2311 | [Process Overload] (OLC)
| 16#2320 | [Motor short circuit] (SCF1)
| 16#2320 | [Motor Short Circuit] (SCF5)
| 16#2330 | [Ground Short Circuit] (SCF3)
| 16#2350 | [Motor Overload] (OLF)
| 16#3110 | [Supply Mains Overvoltage] (OSF)
| 16#3120 | [Supply Mains UnderV] (USF)
| 16#3130 | [Input phase loss] (PHF)
| 16#3280 | [AFE Bus unbalancing] (ObF2)
| 16#3300 | [Single output phase loss] (OPF1)
| 16#3310 | [DC Bus Overvoltage] (ObF)
| 16#3310 | [Output Phase Loss] (OPF2)
| 16#4210 | [Input Overheating] (IHF)
| 16#4210 | [Drive Overheating] (OHF)
| 16#4210 | [IGBT Overheating] (tJF)
| 16#4210 | [AI2 Th Detected Error] (tH2F)
| 16#4210 | [AI3 Th Detected Error] (tH3F)
| 16#4210 | [AI4 Th Detected Error] (tH4F)
| 16#4210 | [AI5 Th Detected Error] (tH5F)
| 16#5000 | [Input Contactor] (LCF)
| 16#5100 | [Internal Error 8] (InF8)
| 16#5100 | [Internal Error 10] (InFA)
| 16#5210 | [Internal Error 9] (InF9)
| 16#5210 | [Internal Error 11] (InFb)
| 16#5210 | [Internal Error 12] (InFC)
| 16#5210 | [Internal Error 13] (InFd)
| 16#5500 | [Internal Error 15] (InFF)
| 16#5530 | [EEPROM Control] (EEF1)
| 16#5530 | [EEPROM Power] (EEF2)
| 16#6100 | [Internal Link Error] (ILF)
| 16#6100 | [Internal Error 1] (InF1)
| 16#6100 | [Internal Error 2] (InF2)
| 16#6100 | [Internal Error 3] (InF3)
| 16#6100 | [Internal Error 4] (InF4)
| 16#6100 | [Internal Error 7] (InF7)
| 16#6100 | [Internal Error 6] (InF6)
| 16#6100 | [Boards Compatibility] (HCF)
| 16#6100 | [Internal Error 0] (InF0)
| 16#6100 | [Internal Error 21] (InFL)
| 16#6100 | [Internal Error 22] (InFM)
| 16#6100 | [Internal Error 25] (InFP)
| 16#6100 | [Internal Error 20] (InF )
| 16#6100 | [Internal Error 27] (InFr)
| 16#6100 | [MonitorCircuit A Error] (IFA)
| 16#6100 | [MonitorCircuit B Error] (IFb)
| 16#6100 | [MonitorCircuit C Error] (IFC)
| 16#6100 | [MonitorCircuit D Error] (IFd)
| 16#6100 | [CabinetCircuit A Error] (CFA)
| 16#6100 | [CabinetCircuit B Error] (CFb)
| 16#6100 | [CabinetCircuit C Error] (CFC)
| 16#6100 | [MotorWinding A Error] (tFA)
| 16#6100 | [MotorWinding B Error] (tFb)
| 16#6100 | [MotorBearing A Error] (tFC)
| 16#6100 | [MotorBearing B Error] (tFd)
| 16#6100 | [Cabinet Overheat Error] (CHF)
| 16#6100 | [AFE Mains Undervoltage] (UrF)
| 16#6100 | [Internal Error 31] (InFU)
| 16#6100 | [Internal Error 29] (InFt)
| 16#6100 | [Internal Error 30] (InFU)
| 16#6100 | [AFE IGBT over-heat error] (tJF2)
| 16#6100 | [AFE contactor feedback error] (CrF3)
| 16#6100 | [AFE Modulation Rate Error] (ACF1)
| 16#6100 | [AFE Current Control Error] (ACF2)
| 16#6100 | [Mains Freq Out Of Range] (MFF)
| 16#6300 | [Incorrect Configuration] (CFF)
| 16#6300 | [Invalid Configuration] (CFI)
| 16#6300 | [Conf Transfer Error] (CFI2)
| 16#6300 | [Pre-settings Transfer Error] (CFI3)
| 16#6300 | [Circuit Breaker Error] (CbF)
| 16#6300 | [Empty Configuration] (CFI4)
| 16#7000 | [Internal Error 16] (InFG)
| 16#7000 | [Internal Error 17] (InFH)
| 16#7000 | [Firmware Update Error] (FWEr)
| 16#7121 | [Motor Stall Error] (StF)
| 16#7300 | [AI2 4-20mA loss] (LFF2)
| 16#7300 | [AI3 4-20mA loss] (LFF3)
| 16#7300 | [AI4 4-20mA loss] (LFF4)
| 16#7300 | [AI5 4-20 mA loss] (LFF5)
| 16#7300 | [AI1 4-20 mA loss] (LFF1)
| 16#7300 | [AI2 Thermal Sensor Error] (t2CF)
| 16#7300 | [AI3 Thermal Sensor Error] (t3CF)
| 16#7300 | [AI4 Thermal Sensor Error] (t4CF)
| 16#7300 | [AI5 Thermal Sensor Error] (t5CF)
| 16#7400 | [Program Loading Error] (PGLF)
| 16#7400 | [Program Running Error] (PGrF)
| 16#7500 | [PID Feedback Error] (PFMF)
| 16#7510 | [Modbus Com Interruption] (SLF1)
| 16#7510 | [HMI Com Interruption] (SLF3)
| 16#7520 | [Fieldbus Com Interrupt] (CnF)
| 16#7530 | [PC Com Interruption] (SLF2)
| 16#7540 | [Embd Eth Com Interrupt] (EtHF)
| 16#8100 | [CANopen Com Interrupt] (COF)
| 16#8800 | [Internal Error 23] (InFn)
| 16#9000 | [External Error] (EPF1)
| 16#9000 | [Fieldbus Error] (EPF2)
| 16#9000 | [FDR 1 Error] (Fdr1)
| 16#9000 | [FDR 2 Error] (Fdr2)
| 16#FF00 | [Autotuning Error] (tnF)
| 16#FF03 | [Process Underload] (ULF)
| 16#FF03 | [Safety Function Error] (SAFF)
| 16#FF11 | [PumpCycle Start Error] (PCPF)
| 16#FF11 | [Inlet Pressure Error] (IPPF)
| 16#FF11 | [Pump Low Flow Error] (PLFF)
| 16#FF11 | [Anti Jam Error] (JAMF)
| 16#FF11 | [Dry Run Error] (drYF)
| 16#FF12 | [Out Pressure Low] (OPLF)
| 16#FF12 | [High Flow Error] (HFPF)
| 16#FF12 | [Out Pressure High] (OPHF)
| 16#FFFF | [Lead Pump Error] (MPLF)
| 16#FFFF | [Low Level Error] (LCLF)
| 16#FFFF | [High Level Error] (LCHF)
| 16#FFFF | [Internal Error 28] (InFS)
| 16#FFFF | [MultiDrive Link Error] (MdLF)
| 16#FFFF | [M/P Device Error] (MPdF)
FCS | 0 | (nO)
| 1 | (rEC0)
| 2 | (rEC1)
| 3 | (rEC2)
| 4 | (rEC3)
| 64 | (InI)
| 71 | (InI1)
FDRA | 0 | [NOT ACTIVE] (IdLE)
| 1 | [SAVE] (SAUE)
| 2 | [REST] (rESt)
FEM | 0 | [No] (nO)
| 1 | [HQ] (Hq)
| 2 | [PQ] (Pq)
FFM | 0 | [Standard] (Std)
| 1 | [Always] (rUn)
| 2 | [Never] (StP)
| 3 | [Economy] (ECO)
FLCM | 0 | [Inactive] (nO)
| 1 | [Display] (MOn)
| 2 | [Compensation] (COMP)
FOR | 2 | [8-O-1] (8o1)
| 3 | [8-E-1] (8E1)
| 4 | [8-N-1] (8n1)
| 5 | [8-N-2] (8n2)
HMIS | 0 | [Autotuning] (tUn)
| 1 | [In DC inject.] (dCb)
| 2 | [Ready] (rdY)
| 3 | [Freewheel] (nSt)
| 4 | [Running] (rUn)
| 5 | [Accelerating] (ACC)
| 6 | [Decelarating] (dEC)
| 7 | [Current limitation] (CLI)
| 8 | [Fast stop] (FSt)
| 11 | [No Mains Voltage] (nLP)
| 13 | [control.stop] (CtL)
| 14 | [Dec. adapt.] (Obr)
| 15 | [Output cut] (SOC)
| 17 | [Undervoltage Warning] (USA)
| 18 | [TC Mode Active] (tC)
| 19 | [In autotest] (St)
| 20 | [Autotest error] (FA)
| 21 | [Autotest OK] (YES)
| 22 | [EEprom test] (EP)
| 23 | ["Operating State ""Fault"" "] (FLt)
| 25 | [DCP Flashing Mode] (dCP)
| 30 | [STO active] (StO)
| 35 | [Energy Saving] (IdLE)
| 36 | [Firmware Update] (FWUP)
| 37 | [AFE Mains Undervoltage] (UrA)
INR | 0 | [0.01] (0.01)
| 1 | [0.1] (0.1)
| 2 | [1] (1)
IPPM | 0 | [No] (nO)
| 1 | [Warning] (ALArM)
| 2 | [Compensation] (COMP)
JATC | 0 | [No] (nO)
| 1 | [Start] (StArt)
| 2 | [Time] (tIME)
| 3 | [Torque] (tOrqUE)
LDD | 0 | [Distrib. Log. DISABLE] (nO)
| 1 | [Motor Frequency] (rFr)
| 2 | [Motor Current] (LCr)
| 3 | [Motor Speed] (SPd)
| 4 | [Motor Voltage] (UOP)
| 5 | [Motor Mech. Power] (OPrW)
| 6 | [Input Elec. Power] (IPrW)
| 7 | [Output Elec. Power] (EPrW)
| 8 | [Motor Torque] (Otr)
| 9 | [Mains Voltage] (ULn)
| 10 | [DC BUS Voltage] (UbUS)
| 11 | [PID feedback] (rPF)
| 12 | [AI2 Th Value] (tH2U)
| 13 | [AI3 Th Value] (tH3U)
| 14 | [AI4 Th Value] (tH4U)
| 15 | [AI5 Th Value] (tH5U)
| 16 | [Drive Thermal State] (tHd)
| 17 | [Motor Thermal State] (tHr)
| 18 | [Installation Flow] (FS1U)
| 19 | [Pump Flow] (FS2U)
| 20 | [Inlet Pressure] (PS1U)
| 21 | [Outlet Pressure] (PS2U)
| 22 | [Energy Consum. Ind.] (ECI)
| 23 | [Pump efficiency] (EFY)
| 24 | [Energy Perf. Ind.] (EPI)
| 25 | [Mains Current] (ILn)
| 26 | [Input Reactive Power] (IqrW)
| 27 | [Input Power Factor] (PWF)
| 28 | [AI1 Th Value] (tH1U)
| 29 | [DBR Thermal State] (tHb)
LDEN | 0 | [Stop] (StOP)
| 1 | [Start] (StArt)
| 2 | [Always] (ALWAYS)
| 3 | [Reset] (rESEt)
| 4 | [Clear] (CLEAr)
| 5 | [Error] (ErrOr)
LDST | 2 | [200 ms] (200MS)
| 10 | [1 second] (1S)
| 20 | [2 seconds] (2S)
| 50 | [5 seconds] (5S)
LFT | 0 | [No Error] (nOF)
| 2 | [EEPROM Control] (EEF1)
| 3 | [Incorrect Configuration] (CFF)
| 4 | [Invalid Configuration] (CFI)
| 5 | [Modbus Com Interruption] (SLF1)
| 6 | [Internal Link Error] (ILF)
| 7 | [Fieldbus Com Interrupt] (CnF)
| 8 | [External Error] (EPF1)
| 9 | [Overcurrent] (OCF)
| 10 | [Precharge Capacitor] (CrF)
| 13 | [AI2 4-20mA loss] (LFF2)
| 15 | [Input Overheating] (IHF)
| 16 | [Drive Overheating] (OHF)
| 17 | [Motor Overload] (OLF)
| 18 | [DC Bus Overvoltage] (ObF)
| 19 | [Supply Mains Overvoltage] (OSF)
| 20 | [Single output phase loss] (OPF1)
| 21 | [Input phase loss] (PHF)
| 22 | [Supply Mains UnderV] (USF)
| 23 | [Motor short circuit] (SCF1)
| 24 | [Motor Overspeed] (SOF)
| 25 | [Autotuning Error] (tnF)
| 26 | [Internal Error 1] (InF1)
| 27 | [Internal Error 2] (InF2)
| 28 | [Internal Error 3] (InF3)
| 29 | [Internal Error 4] (InF4)
| 30 | [EEPROM Power] (EEF2)
| 32 | [Ground Short Circuit] (SCF3)
| 33 | [Output Phase Loss] (OPF2)
| 34 | [CANopen Com Interrupt] (COF)
| 37 | [Internal Error 7] (InF7)
| 38 | [Fieldbus Error] (EPF2)
| 40 | [Internal Error 8] (InF8)
| 42 | [PC Com Interruption] (SLF2)
| 45 | [HMI Com Interruption] (SLF3)
| 51 | [Internal Error 9] (InF9)
| 52 | [Internal Error 10] (InFA)
| 53 | [Internal Error 11] (InFb)
| 54 | [IGBT Overheating] (tJF)
| 55 | [IGBT Short Circuit] (SCF4)
| 56 | [Motor Short Circuit] (SCF5)
| 60 | [Internal Error 12] (InFC)
| 64 | [Input Contactor] (LCF)
| 68 | [Internal Error 6] (InF6)
| 69 | [Internal Error 14] (InFE)
| 71 | [AI3 4-20mA loss] (LFF3)
| 72 | [AI4 4-20mA loss] (LFF4)
| 73 | [Boards Compatibility] (HCF)
| 77 | [Conf Transfer Error] (CFI2)
| 79 | [AI5 4-20 mA loss] (LFF5)
| 99 | [Channel Switch Error] (CSF)
| 100 | [Process Underload] (ULF)
| 101 | [Process Overload] (OLC)
| 105 | [Angle error] (ASF)
| 106 | [AI1 4-20 mA loss] (LFF1)
| 107 | [Safety Function Error] (SAFF)
| 110 | [AI2 Th Detected Error] (tH2F)
| 111 | [AI2 Thermal Sensor Error] (t2CF)
| 112 | [AI3 Th Detected Error] (tH3F)
| 113 | [AI3 Thermal Sensor Error] (t3CF)
| 114 | [PumpCycle Start Error] (PCPF)
| 115 | [Out Pressure Low] (OPLF)
| 116 | [High Flow Error] (HFPF)
| 117 | [Inlet Pressure Error] (IPPF)
| 119 | [Pump Low Flow Error] (PLFF)
| 120 | [AI4 Th Detected Error] (tH4F)
| 121 | [AI4 Thermal Sensor Error] (t4CF)
| 122 | [AI5 Th Detected Error] (tH5F)
| 123 | [AI5 Thermal Sensor Error] (t5CF)
| 124 | [Anti Jam Error] (JAMF)
| 125 | [Out Pressure High] (OPHF)
| 126 | [Dry Run Error] (drYF)
| 127 | [PID Feedback Error] (PFMF)
| 128 | [Program Loading Error] (PGLF)
| 129 | [Program Running Error] (PGrF)
| 130 | [Lead Pump Error] (MPLF)
| 131 | [Low Level Error] (LCLF)
| 132 | [High Level Error] (LCHF)
| 142 | [Internal Error 16] (InFG)
| 143 | [Internal Error 17] (InFH)
| 144 | [Internal Error 0] (InF0)
| 146 | [Internal Error 13] (InFd)
| 148 | [Motor Stall Error] (StF)
| 149 | [Internal Error 21] (InFL)
| 150 | [Embd Eth Com Interrupt] (EtHF)
| 151 | [Internal Error 15] (InFF)
| 152 | [Firmware Update Error] (FWEr)
| 153 | [Internal Error 22] (InFM)
| 154 | [Internal Error 25] (InFP)
| 155 | [Internal Error 20] (InF )
| 157 | [Internal Error 27] (InFr)
| 158 | [Internal Error 23] (InFn)
| 159 | [AFE ShortCircuit error] (SCF6)
| 160 | [AFE Bus unbalancing] (ObF2)
| 161 | [Internal Error 28] (InFS)
| 162 | [MonitorCircuit A Error] (IFA)
| 163 | [MonitorCircuit B Error] (IFb)
| 164 | [MonitorCircuit C Error] (IFC)
| 165 | [MonitorCircuit D Error] (IFd)
| 166 | [CabinetCircuit A Error] (CFA)
| 167 | [CabinetCircuit B Error] (CFb)
| 168 | [CabinetCircuit C Error] (CFC)
| 169 | [MotorWinding A Error] (tFA)
| 170 | [MotorWinding B Error] (tFb)
| 171 | [MotorBearing A Error] (tFC)
| 172 | [MotorBearing B Error] (tFd)
| 173 | [Cabinet Overheat Error] (CHF)
| 174 | [AFE Mains Undervoltage] (UrF)
| 175 | [Internal Error 31] (InFU)
| 176 | [Internal Error 29] (InFt)
| 177 | [Internal Error 30] (InFU)
| 179 | [AFE IGBT over-heat error] (tJF2)
| 180 | [AFE contactor feedback error] (CrF3)
| 181 | [Pre-settings Transfer Error] (CFI3)
| 182 | [Circuit Breaker Error] (CbF)
| 186 | [MultiDrive Link Error] (MdLF)
| 190 | [M/P Device Error] (MPdF)
| 191 | [AFE Modulation Rate Error] (ACF1)
| 192 | [AFE Current Control Error] (ACF2)
| 193 | [Mains Freq Out Of Range] (MFF)
| 196 | [Empty Configuration] (CFI4)
| 200 | [FDR 1 Error] (Fdr1)
| 201 | [FDR 2 Error] (Fdr2)
MPC | 0 | [Mot Power] (nPr)
| 1 | [Mot Cosinus] (COS)
MPDT | 0 | [Slave] (SLAUE)
| 1 | [Master] (MASt)
MPST | 0 | [Standard] (tMC)
| 1 | [Distributed] (dMC)
| 2 | [Advanced] (AMC)
| 3 | [Synchronized] (SYnC)
N_Y | 0 | [No] (nO)
| 1 | [Yes] (YES)
NCV | 0 | [Unknown rating] (nO)
| 1 | [0.12kW] (U01)
| 2 | [0.18kW / 0.25Hp] (U02)
| 3 | [0.25kW] (U03)
| 4 | [0.37 kW / 0.5 Hp] (U04)
| 5 | [0.55 kW /0.75 Hp] (U05)
| 6 | [0.75 kW / 1 Hp] (U07)
| 7 | [5.5kW / 7.5HP] (U09)
| 8 | [1.1 kW / 1.5 Hp] (U11)
| 9 | [1.5 kW / 2 Hp] (U15)
| 10 | [1.85kW] (U18)
| 11 | [2.2 kW / 3 Hp] (U22)
| 12 | [3 kW / 4HP] (U30)
| 13 | [4kW / 5HP] (U37)
| 14 | [4kW / 5HP] (U40)
| 15 | [5.5 kW / 7.5 Hp] (U55)
| 16 | [7.5 kW / 10 Hp] (U75)
| 17 | [9kW] (U90)
| 18 | [11 kW / 15 Hp] (d11)
| 19 | [15 kW / 20 Hp] (d15)
| 20 | [18,5kW / 25HP] (d18)
| 21 | [22kW / 30HP] (d22)
| 22 | [30kW / 40HP] (d30)
| 23 | [37kW / 50HP] (d37)
| 24 | [45kW / 60HP] (d45)
| 25 | [55kW / 75HP] (d55)
| 26 | [75kW / 100HP] (d75)
| 27 | [90kW / 125HP] (d90)
| 28 | [110 kW / 150HP] (C11)
| 29 | [132kW / 200 HP] (C13)
| 30 | [160kW / 250HP] (C16)
| 31 | [200kW / 300HP] (C20)
| 32 | [220kW / 350HP] (C22)
| 33 | [250kW / 400HP] (C25)
| 34 | [280kW / 450HP] (C28)
| 35 | [315kW / 500HP] (C31)
| 36 | [355 kW / 450HP] (C35)
| 37 | [400kW / 600HP] (C40)
| 38 | [450kW / 750HP] (C45)
| 39 | [500kW / 800HP] (C50)
| 40 | [560kW / 850HP] (C56)
| 41 | [630kW / 900HP] (C63)
| 42 | [710kW / 950HP] (C71)
| 43 | [800kW / 1000HP] (C80)
NPL | 0 | [1] (POS)
| 1 | [0] (nEG)
OPL | 0 | [Function Inactive] (nO)
| 1 | [OPF Error Triggered] (YES)
| 2 | [No Error Triggered] (OAC)
OPPM | 0 | [No] (nO)
| 1 | [Switch] (SW)
| 2 | [Sensor] (SnSr)
| 3 | [Both] (bOtH)
PCM | 0 | [No] (nO)
| 1 | [HQ] (Hq)
| 2 | [PQ] (Pq)
| 3 | [PHQ] (PHq)
PCPM | 0 | [No] (nO)
| 1 | [Mode 1] (nOrM)
| 2 | [Mode 2] (rtC)
PCS | 0 | [None] (nOnE)
| 1 | [Inactive] (nACt)
| 2 | [Active] (ACtIUE)
| 3 | [Failed] (FAILEd)
PFM | 0 | [No] (nO)
| 1 | [Feedback] (Fb )
| 2 | [Outlet Pressure] (PS2)
PHR | 0 | [ABC] (AbC)
| 1 | [ACB] (ACb)
PLFM | 0 | [No] (nO)
| 1 | [Switch] (SW)
| 2 | [Flow] (q)
| 3 | [Flow vs Speed] (qn)
| 5 | [No Flow Power] (nF)
PRFL | 0 | (UnCG)
| 1 | (1)
| 100 | (100)
| 101 | (101)
| 102 | (102)
| 106 | (106)
| 107 | (107)
PSA | 0 | [Not Configured] (nO)
| 1 | [AI1] (AI1)
| 2 | [AI2] (AI2)
| 3 | [AI3] (AI3)
| 4 | [AI4] (AI4)
| 5 | [AI5] (AI5)
| 129 | [Motor Current] (OCr)
| 130 | [Motor Frequency] (OFr)
| 131 | [Ramp out.] (OrP)
| 132 | [Motor torq.] (trq)
| 133 | [Sign. torque] (Stq)
| 134 | [sign ramp] (OrS)
| 135 | [PID ref.] (OPS)
| 136 | [PID feedbk] (OPF)
| 137 | [PID error] (OPE)
| 138 | [PID output] (OPI)
| 139 | [Drive Power] (OPr)
| 140 | [Mot thermal] (tHr)
| 141 | [Drv thermal] (tHd)
| 160 | [Ref Frequency via DI] (UPdt)
| 163 | [Ref.Freq-Rmt.Term] (LCC)
| 164 | [Ref. Freq-Modbus] (Mdb)
| 167 | [Ref. Freq-CANopen] (CAn)
| 169 | [Ref. Freq-Com. Module] (nEt)
| 171 | [Embedded Ethernet] (EtH)
| 173 | [Sig. o/p frq.] (OFS)
| 180 | [Motor volt.] (UOP)
| 183 | [AI Virtual 1] (AIU1)
| 185 | [AI Virtual 2] (AIU2)
| 186 | [DI5 PulseInput Assignment] (PI5)
| 187 | [DI6 PulseInput Assignment] (PI6)
| 197 | [AI Virtual 3] (AIU3)
| 340 | [Estimated Pump Flow] (SLPF)
| 341 | [Inlet Pressure Value] (PS1U)
| 342 | [Outlet Pressure Value] (PS2U)
| 343 | [Installation Flow] (FS1U)
| 346 | [Estimated Sys Flow] (SLSF)
PSL | 0 | [Not Assigned] (nO)
| 1 | [Operating State Fault] (FLt)
| 2 | [Drive Running] (rUn)
| 4 | [Mot Freq High Thd] (FtA)
| 5 | [High Speed Reached] (FLA)
| 6 | [Current Thd Reached] (CtA)
| 7 | [Ref Freq Reached] (SrA)
| 8 | [Motor Therm Thd reached] (tSA)
| 10 | [PID error Warning] (PEE)
| 11 | [PID feedback Warning] (PFA)
| 12 | [AI2 4-20 Loss Warning] (AP2)
| 13 | [Mot Freq High Thd 2] (F2A)
| 14 | [Drv Therm Thd reached] (tAd)
| 16 | [Ref Freq High Thd reached] (rtAH)
| 17 | [Ref Freq Low Thd reached] (rtAL)
| 18 | [Mot Freq Low Thd] (FtAL)
| 19 | [Mot Freq Low Thd 2] (F2AL)
| 20 | [Low Current Reached] (CtAL)
| 21 | [Process Undld Warning] (ULA)
| 22 | [Process Overload Warning] (OLA)
| 23 | [PID High Fdbck Warning] (PFAH)
| 24 | [PID Low Fdbck Warning] (PFAL)
| 25 | [Regulation Warning] (PISH)
| 28 | [High Torque Warning] (ttHA)
| 29 | [Low Torque Warning] (ttLA)
| 30 | [Forward] (MFrd)
| 31 | [Reverse] (MrrS)
| 34 | [Ramp switching] (rP2)
| 47 | [Neg Torque] (AtS)
| 48 | [Cnfg.0 act.] (CnF0)
| 52 | [set 1 active] (CFP1)
| 53 | [set 2 active] (CFP2)
| 54 | [set 3 active] (CFP3)
| 55 | [set 4 active] (CFP4)
| 64 | [DC charged] (dbL)
| 66 | [Power Removal State] (PrM)
| 73 | [Mains Contactor] (LLC)
| 77 | [I present] (MCP)
| 80 | [Warning Grp 1] (AG1)
| 81 | [Warning Grp 2] (AG2)
| 82 | [Warning Grp 3] (AG3)
| 87 | [External Error Warning] (EFA)
| 88 | [Undervoltage Warning] (USA)
| 89 | [Preventive UnderV Active] (UPA)
| 91 | [Drive Thermal Warning] (tHA)
| 92 | [AFE Mains Undervoltage] (UrA)
| 96 | [Ref Freq Channel 1] (Fr1)
| 97 | [Ref Freq Channel 2] (Fr2)
| 98 | [Cmd Channel 1] (Cd1)
| 99 | [Cmd Channel 2] (Cd2)
| 100 | [ch1B active] (Fr1b)
| 104 | [IGBT Thermal Warning] (tJA)
| 107 | [AI3 4-20 Loss Warning] (AP3)
| 108 | [AI4 4-20 Loss Warning] (AP4)
| 110 | [Flow Limit Active] (FSA)
| 116 | [Function key 1] (Fn1)
| 117 | [Function key 2] (Fn2)
| 118 | [Function key 3] (Fn3)
| 119 | [Function key 4] (Fn4)
| 123 | [AI1 4-20 Loss Warning] (AP1)
| 127 | [Ready] (rdY)
| 128 | [Yes] (YES)
| 129 | [DI1] (LI1)
| 130 | [DI2] (LI2)
| 131 | [DI3] (LI3)
| 132 | [DI4] (LI4)
| 133 | [DI5] (LI5)
| 134 | [DI6] (LI6)
| 139 | [DI11] (LI11)
| 140 | [DI12] (LI12)
| 141 | [DI13] (LI13)
| 142 | [DI14] (LI14)
| 143 | [DI15] (LI15)
| 144 | [DI16] (LI16)
| 160 | [CD00] (Cd00)
| 161 | [CD01] (Cd01)
| 162 | [CD02] (Cd02)
| 163 | [CD03] (Cd03)
| 164 | [CD04] (Cd04)
| 165 | [CD05] (Cd05)
| 166 | [CD06] (Cd06)
| 167 | [CD07] (Cd07)
| 168 | [CD08] (Cd08)
| 169 | [CD09] (Cd09)
| 170 | [CD10] (Cd10)
| 171 | [CD11] (Cd11)
| 172 | [CD12] (Cd12)
| 173 | [CD13] (Cd13)
| 174 | [CD14] (Cd14)
| 175 | [CD15] (Cd15)
| 176 | [C100] (C100)
| 177 | [C101] (C101)
| 178 | [C102] (C102)
| 179 | [C103] (C103)
| 180 | [C104] (C104)
| 181 | [C105] (C105)
| 182 | [C106] (C106)
| 183 | [C107] (C107)
| 184 | [C108] (C108)
| 185 | [C109] (C109)
| 186 | [C110] (C110)
| 187 | [C111] (C111)
| 188 | [C112] (C112)
| 189 | [C113] (C113)
| 190 | [C114] (C114)
| 191 | [C115] (C115)
| 192 | [C200] (C200)
| 193 | [C201] (C201)
| 194 | [C202] (C202)
| 195 | [C203] (C203)
| 196 | [C204] (C204)
| 197 | [C205] (C205)
| 198 | [C206] (C206)
| 199 | [C207] (C207)
| 200 | [C208] (C208)
| 201 | [C209] (C209)
| 202 | [C210] (C210)
| 203 | [C211] (C211)
| 204 | [C212] (C212)
| 205 | [C213] (C213)
| 206 | [C214] (C214)
| 207 | [C215] (C215)
| 208 | [C300] (C300)
| 209 | [C301] (C301)
| 210 | [C302] (C302)
| 211 | [C303] (C303)
| 212 | [C304] (C304)
| 213 | [C305] (C305)
| 214 | [C306] (C306)
| 215 | [C307] (C307)
| 216 | [C308] (C308)
| 217 | [C309] (C309)
| 218 | [C310] (C310)
| 219 | [C311] (C311)
| 220 | [C312] (C312)
| 221 | [C313] (C313)
| 222 | [C314] (C314)
| 223 | [C315] (C315)
| 240 | [C500] (C500)
| 241 | [C501] (C501)
| 242 | [C502] (C502)
| 243 | [C503] (C503)
| 244 | [C504] (C504)
| 245 | [C505] (C505)
| 246 | [C506] (C506)
| 247 | [C507] (C507)
| 248 | [C508] (C508)
| 249 | [C509] (C509)
| 250 | [C510] (C510)
| 251 | [C511] (C511)
| 252 | [C512] (C512)
| 253 | [C513] (C513)
| 254 | [C514] (C514)
| 255 | [C515] (C515)
| 272 | [DI1 (Low level)] (L1L)
| 273 | [DI2 (Low level)] (L2L)
| 274 | [DI3 (Low level)] (L3L)
| 275 | [DI4 (Low level)] (L4L)
| 276 | [DI5 (Low level)] (L5L)
| 277 | [DI6 (Low level)] (L6L)
| 282 | [DI11 (Low level)] (L11L)
| 283 | [DI12 (Low level)] (L12L)
| 284 | [DI13 (Low level)] (L13L)
| 285 | [DI14 (Low level)] (L14L)
| 286 | [DI15 (Low level)] (L15L)
| 287 | [DI16 (Low level)] (L16L)
| 302 | [DI50 (High Level)] (d50H)
| 303 | [DI51 (High Level)] (d51H)
| 304 | [DI52 (High Level)] (d52H)
| 305 | [DI53 (High Level)] (d53H)
| 306 | [DI54 (High Level)] (d54H)
| 307 | [DI55 (High Level)] (d55H)
| 308 | [DI56 (High Level)] (d56H)
| 309 | [DI57 (High Level)] (d57H)
| 310 | [DI58 (High Level)] (d58H)
| 311 | [DI59 (High Level)] (d59H)
| 312 | [DI50 (Low level)] (d50L)
| 313 | [DI51 (Low level)] (d51L)
| 314 | [DI52 (Low level)] (d52L)
| 315 | [DI53 (Low level)] (d53L)
| 316 | [DI54 (Low level)] (d54L)
| 317 | [DI55 (Low level)] (d55L)
| 318 | [DI56 (Low level)] (d56L)
| 319 | [DI57 (Low level)] (d57L)
| 320 | [DI58 (Low level)] (d58L)
| 321 | [DI59 (Low level)] (d59L)
| 340 | [Jockey] (JO Y)
| 341 | [Priming] (PrIM)
| 342 | [Anti-Jam Active] (JAMr)
| 344 | [Pipe Fill] (FILL)
| 345 | [Priming Pump Active] (PPOn)
| 346 | [Dry Run Warning] (drYA)
| 347 | [Pump Low Flow] (PLFA)
| 348 | [Proc High Flow Warning] (HFPA)
| 349 | [InPress Warning] (IPPA)
| 350 | [Low OutPres Warning] (OPLA)
| 351 | [High OutPres Warning] (OPHA)
| 352 | [Pump Cycle Warning] (PCPA)
| 353 | [Anti-Jam Warning] (JAMA)
| 354 | [Low Flow Warning] (LFA)
| 355 | [Low Pressure Warning] (LPA)
| 356 | [Switch OutPres Warning] (OPSA)
| 357 | [Jockey Pump Active] (JPOn)
| 358 | [Pump 1 Cmd] (MPO1)
| 359 | [Pump 2 Cmd] (MPO2)
| 360 | [Pump 3 Cmd] (MPO3)
| 361 | [Pump 4 Cmd] (MPO4)
| 362 | [Pump 5 Cmd] (MPO5)
| 363 | [Pump 6 Cmd] (MPO6)
| 364 | [MultiPump Capacity Warn] (MPCA)
| 365 | [Lead Pump Warn] (MPLA)
| 366 | [High Level Warning] (LCHA)
| 367 | [Low Level Warning] (LCLA)
| 368 | [Level Switch Warning] (LCWA)
| 369 | [M/P Device Warn] (MPdA)
| 484 | [Cust Warning 5] (CAS5)
| 488 | [Cabinet Fan Command] (FCC)
| 489 | [CB Start Pulse] (CbEP)
| 490 | [CB Stop Pulse] (CbdP)
| 491 | [Power Cons Warning] (POWd)
| 492 | [Warning Grp 4] (AG4)
| 493 | [Warning Grp 5] (AG5)
| 494 | [Fallback speed] (FrF)
| 495 | [Speed Maintained] (rLS)
| 496 | [Per Type of Stop] (Stt)
| 497 | [Life Cycle Warn 1] (LCA1)
| 498 | [Life Cycle Warn 2] (LCA2)
| 499 | [AI2 Th Warning] (tP2A)
| 500 | [AI3 Th Warning] (tP3A)
| 501 | [AI4 Th Warning] (tP4A)
| 502 | [AI5 Th Warning] (tP5A)
| 503 | [AI5 4-20 Loss Warning] (AP5)
| 504 | [Fan Counter Warning] (FCtA)
| 505 | [Fan Feedback Warning] (FFdA)
| 506 | [Power High Threshold] (PtHA)
| 507 | [Power Low Threshold] (PtHL)
| 508 | [Cust Warning 1] (CAS1)
| 509 | [Cust Warning 2] (CAS2)
| 510 | [Cust Warning 3] (CAS3)
| 511 | [Cust Warning 4] (CAS4)
PSLIN | 0 | [Not Assigned] (nO)
| 1 | [Operating State Fault] (FLt)
| 4 | [Mot Freq High Thd] (FtA)
| 13 | [Mot Freq High Thd 2] (F2A)
| 18 | [Mot Freq Low Thd] (FtAL)
| 19 | [Mot Freq Low Thd 2] (F2AL)
| 96 | [Ref Freq Channel 1] (Fr1)
| 97 | [Ref Freq Channel 2] (Fr2)
| 98 | [Cmd Channel 1] (Cd1)
| 99 | [Cmd Channel 2] (Cd2)
| 100 | [ch1B active] (Fr1b)
| 128 | [Yes] (YES)
| 129 | [DI1] (LI1)
| 130 | [DI2] (LI2)
| 131 | [DI3] (LI3)
| 132 | [DI4] (LI4)
| 133 | [DI5] (LI5)
| 134 | [DI6] (LI6)
| 139 | [DI11] (LI11)
| 140 | [DI12] (LI12)
| 141 | [DI13] (LI13)
| 142 | [DI14] (LI14)
| 143 | [DI15] (LI15)
| 144 | [DI16] (LI16)
| 160 | [CD00] (Cd00)
| 161 | [CD01] (Cd01)
| 162 | [CD02] (Cd02)
| 163 | [CD03] (Cd03)
| 164 | [CD04] (Cd04)
| 165 | [CD05] (Cd05)
| 166 | [CD06] (Cd06)
| 167 | [CD07] (Cd07)
| 168 | [CD08] (Cd08)
| 169 | [CD09] (Cd09)
| 170 | [CD10] (Cd10)
| 171 | [CD11] (Cd11)
| 172 | [CD12] (Cd12)
| 173 | [CD13] (Cd13)
| 174 | [CD14] (Cd14)
| 175 | [CD15] (Cd15)
| 177 | [C101] (C101)
| 178 | [C102] (C102)
| 179 | [C103] (C103)
| 180 | [C104] (C104)
| 181 | [C105] (C105)
| 182 | [C106] (C106)
| 183 | [C107] (C107)
| 184 | [C108] (C108)
| 185 | [C109] (C109)
| 186 | [C110] (C110)
| 187 | [C111] (C111)
| 188 | [C112] (C112)
| 189 | [C113] (C113)
| 190 | [C114] (C114)
| 191 | [C115] (C115)
| 193 | [C201] (C201)
| 194 | [C202] (C202)
| 195 | [C203] (C203)
| 196 | [C204] (C204)
| 197 | [C205] (C205)
| 198 | [C206] (C206)
| 199 | [C207] (C207)
| 200 | [C208] (C208)
| 201 | [C209] (C209)
| 202 | [C210] (C210)
| 203 | [C211] (C211)
| 204 | [C212] (C212)
| 205 | [C213] (C213)
| 206 | [C214] (C214)
| 207 | [C215] (C215)
| 209 | [C301] (C301)
| 210 | [C302] (C302)
| 211 | [C303] (C303)
| 212 | [C304] (C304)
| 213 | [C305] (C305)
| 214 | [C306] (C306)
| 215 | [C307] (C307)
| 216 | [C308] (C308)
| 217 | [C309] (C309)
| 218 | [C310] (C310)
| 219 | [C311] (C311)
| 220 | [C312] (C312)
| 221 | [C313] (C313)
| 222 | [C314] (C314)
| 223 | [C315] (C315)
| 241 | [C501] (C501)
| 242 | [C502] (C502)
| 243 | [C503] (C503)
| 244 | [C504] (C504)
| 245 | [C505] (C505)
| 246 | [C506] (C506)
| 247 | [C507] (C507)
| 248 | [C508] (C508)
| 249 | [C509] (C509)
| 250 | [C510] (C510)
| 251 | [C511] (C511)
| 252 | [C512] (C512)
| 253 | [C513] (C513)
| 254 | [C514] (C514)
| 255 | [C515] (C515)
| 272 | [DI1 (Low level)] (L1L)
| 273 | [DI2 (Low level)] (L2L)
| 274 | [DI3 (Low level)] (L3L)
| 275 | [DI4 (Low level)] (L4L)
| 276 | [DI5 (Low level)] (L5L)
| 277 | [DI6 (Low level)] (L6L)
| 282 | [DI11 (Low level)] (L11L)
| 283 | [DI12 (Low level)] (L12L)
| 284 | [DI13 (Low level)] (L13L)
| 285 | [DI14 (Low level)] (L14L)
| 286 | [DI15 (Low level)] (L15L)
| 287 | [DI16 (Low level)] (L16L)
| 302 | [DI50 (High Level)] (d50H)
| 303 | [DI51 (High Level)] (d51H)
| 304 | [DI52 (High Level)] (d52H)
| 305 | [DI53 (High Level)] (d53H)
| 306 | [DI54 (High Level)] (d54H)
| 307 | [DI55 (High Level)] (d55H)
| 308 | [DI56 (High Level)] (d56H)
| 309 | [DI57 (High Level)] (d57H)
| 310 | [DI58 (High Level)] (d58H)
| 311 | [DI59 (High Level)] (d59H)
| 312 | [DI50 (Low level)] (d50L)
| 313 | [DI51 (Low level)] (d51L)
| 314 | [DI52 (Low level)] (d52L)
| 315 | [DI53 (Low level)] (d53L)
| 316 | [DI54 (Low level)] (d54L)
| 317 | [DI55 (Low level)] (d55L)
| 318 | [DI56 (Low level)] (d56L)
| 319 | [DI57 (Low level)] (d57L)
| 320 | [DI58 (Low level)] (d58L)
| 321 | [DI59 (Low level)] (d59L)
PSS | 0 | [Not locked] (nACt)
| 1 | [Locked] (ACt)
QSTD | 2 | (FSt2)
| 6 | (FSt6)
RDS | 0 | [Auto] (AUtO)
| 1 | [10M. full] (10F)
| 2 | [10M. half] (10H)
| 3 | [100M. full] (100F)
| 4 | [100M. half] (100H)
RFQ | 2147483648 | [Not Available] (Und)
RPR | 0 | [No] (nO)
| 2 | [Run Time Reset] (rtH)
| 3 | [Internal Run Time Reset] (rtHI)
| 4 | [Power ON Time Reset] (PtH)
| 7 | [Reset Fan Counter] (FtH)
| 8 | [In Power ON Time Reset] (PtHI)
| 9 | [Clear GTHI] (GtHI)
| 10 | [Clear LTHI] (LtHI)
| 11 | [Clear NSM] (nSM)
| 12 | [Clear NSMI] (nSMI)
| 13 | [Clear AFE Fan] (FbAt)
| 14 | [Clear Cabinet Fan] (FCt)
| 20 | [Efficiency MAX] (EFY )
| 21 | [Efficiency MIN] (EFYJ)
| 22 | [Flow Rate MAX] (FS1 )
| 23 | [Flow Rate MIN] (FS1J)
| 24 | [Reset Total Quantity] (FS1C)
| 30 | [Clear BRTH] (brtH)
| 31 | [Clear BRTI] (brtI)
| 32 | [Clear AFE Power ON Time] (bPtH)
| 33 | [Clear BPTI] (bPtI)
| 34 | [Clear AFE Nb. start] (bnSA)
| 35 | [Clear BNSI] (bnSI)
| 36 | [Clear AFE Regen Time] (bGtH)
| 37 | [Clear BGTI] (bGtI)
| 38 | [Clear BLMI] (bLMI)
| 39 | [Clear BLGI] (bLGI)
| 64 | [Reset all] (ALL)
RPT | 0 | [Linear] (LIn)
| 1 | [S-Ramp] (S)
| 2 | [U-Ramp] (U)
| 3 | [Customized] (CUS)
SCS | 0 | [No] (nO)
| 1 | [Config 0] (Str0)
| 2 | [Config 1] (Str1)
| 3 | [Config 2] (Str2)
| 4 | [Config 3] (Str3)
SFDR | 0 | [Initialization] (InIt)
| 1 | [Not Active] (IdLE)
| 2 | [Operational] (OPE)
| 4 | [Ready] (rdY)
| 5 | [IP Configuration] (IPC)
| 7 | [Not Configured] (UnCF)
| 8 | [Reading Configuration] (GEt)
| 9 | [Writing Configuration] (SEt)
| 10 | [Applying Configuration] (APP)
SFT | 1 | [SFR type 1] (HF1)
| 2 | [SFR type 2] (HF2)
SLPM | 0 | [No] (nO)
| 1 | [Switch] (SW)
| 2 | [Flow] (LF)
| 3 | [Speed] (SPd)
| 4 | [Power] (PWr)
| 5 | [Pressure] (HP)
| 6 | [Multiple] (Or)
SMOT | 0 | [No info.] (nO)
| 1 | [Low salient] (LLS)
| 2 | [Med salient] (MLS)
| 3 | [High salient] (HLS)
SOP | 6 | [6 ms] (6)
| 8 | [8 ms] (8)
| 10 | [10 ms] (10)
STOS | 0 | [Not active] (IdLE)
| 1 | [Active] (StO)
| 2 | [Error] (FLt)
STP | 0 | [Inactive] (nO)
| 1 | [Maintain DC Bus] (MMS)
| 2 | [Ramp Stop] (rMP)
| 4 | [Freewheel Stop] (LnF)
STR | 0 | [No Save] (nO)
| 1 | [Save to RAM] (rAM)
| 2 | [Save to EEPROM] (EEP)
STT | 0 | [On Ramp] (rMP)
| 1 | [Fast stop] (FSt)
| 2 | [Freewheel Stop] (nSt)
| 3 | [DC injection] (dCI)
STUN | 0 | [Default] (tAb)
| 1 | [Measure] (MEAS)
| 2 | [Custom] (CUS)
SUCU | 0 | [Euro] (EUrO)
| 1 | [$] (dOLLAr)
| 2 | [£] (POUnd)
| 3 | [Krone] ( r)
| 4 | [Renminbi] (rMb)
| 5 | [Other] (OtHEr)
SUFR | 0 | [1 L/s] (1LS)
| 1 | [0.1 l/s] (01LS)
| 2 | [1 L/mn] (1LM)
| 3 | [1 L/h] (1LH)
| 4 | [1 dm3/mn] (1dM3M)
| 5 | [1 m3/s] (1M3S)
| 6 | [0.1 m3/s] (01M3S)
| 7 | [1 m3/mn] (1M3Mn)
| 8 | [0.1 m3/mn] (01M3Mn)
| 9 | [1 m3/h] (1M3H)
| 10 | [0.1 m3/h] (01M3H)
| 11 | [1 gal/s] (1GPS)
| 12 | [1 GPM] (1GPM)
| 13 | [1 gal/h] (1GPH)
| 14 | [1 ft3/s] (1CFS)
| 15 | [1 CFM] (1CFM)
| 16 | [1 SCFM] (1SCFM)
| 17 | [1 ft3/h] (1CFH)
| 18 | [1 Kg/s] (1 GS)
| 19 | [1 Kg/mn] (1 GM)
| 20 | [1 Kg/h] (1 GH)
| 21 | [1 Lb/s] (1LbS)
| 22 | [1 Lb/mn] (1LbM)
| 23 | [1 Lb/h] (1LbH)
| 24 | [0.1 %] (01PC)
| 25 | [0.1] (01WO)
SUPR | 0 | [1 Kpa] (1 PA)
| 1 | [1 mbar] (1MbAr)
| 2 | [1 Bar] (1bAr)
| 3 | [0.1 Bar] (01bAr)
| 4 | [0.01 Bar] (001bAr)
| 5 | [1 Psi] (1PSI)
| 6 | [0.1 Psi] (01PSI)
| 7 | [1 Psig] (1PSIG)
| 8 | [0.1 Psig] (01PSIG)
| 9 | [1 inH2O] (1InH20)
| 10 | [1 inWg] (1InWG)
| 11 | [1 inWC] (1InWC)
| 12 | [1 ftWg] (1FtWG)
| 13 | [1 ftWc] (1FtWC)
| 14 | [1 ft] (1Ft)
| 15 | [1 mWg] (1MWG)
| 16 | [0.1 mWg] (01MWG)
| 17 | [1 mWC] (1MWC)
| 18 | [0.1 mWc] (01MWC)
| 19 | [1 m] (1M)
| 20 | [0.1 m] (01M)
| 21 | [1 inHg] (1InHG)
| 22 | [0.1 %] (01PC)
| 23 | [0.1] (01WO)
SUTP | 0 | [0.1°C] (01C)
| 1 | [0.1°F] (01F)
| 2 | [0.1 %] (01PC)
| 3 | [0.1] (01WO)
TBR | 4 | [Automatic] (AUtO)
| 8 | [300 bps] (300)
| 12 | [600 bps] (600)
| 16 | [1.2 Kbps] (1 2)
| 20 | [2.4 Kbps] (2 4)
| 24 | [4800 bps] (4 8)
| 28 | [9600 bps] (9 6)
| 30 | [10 Kbps] (10 )
| 32 | [19200 bps] (19 2)
| 34 | [20 Kbps] (20 )
| 35 | [28.8 Kbps] (28 8)
| 36 | [38.4 Kbps] (38 4)
| 37 | [45.45 Kbps] (45 4)
| 38 | [50 Kbps] (50 )
| 40 | [57.6 Kbps] (57 6)
| 42 | [93.75 Kbps] (93 7)
| 44 | [100 Kbps] (100 )
| 48 | [115.2 Kbps] (115 )
| 52 | [125 Kbps] (125 )
| 53 | [156 Kbps] (156 )
| 54 | [187.5 Kbps] (187 )
| 56 | [230.4 Kbps] (230 )
| 60 | [250 Kbps] (250 )
| 64 | [460.8 Kbps] (460 )
| 68 | [500 Kbps] (500 )
| 69 | [625 Kbps] (625 )
| 70 | [800 Kbps] (800 )
| 72 | [921.6 Kbps] (921 )
| 76 | [1 Mbps] (1M)
| 80 | [1.5 Mbps] (1M5)
| 81 | [2.5 Mbps] (2M5)
| 82 | [3 Mbps] (3M)
| 83 | [6 Mbps] (6M)
| 84 | [10 Mbps] (10M)
| 86 | [5 Mbps] (5M)
| 88 | [12 Mbps] (12M)
| 92 | [100 Mbps] (100M)
TCC | 0 | [2-Wire Control] (2C)
| 1 | [3-Wire Control] (3C)
TCT | 0 | [Level] (LEL)
| 1 | [Transition] (trn)
| 2 | [Level With Fwd Priority] (PFO)
THT | 0 | [No] (nO)
| 1 | [Self cooled] (ACL)
| 2 | [Force-cool] (FCL)
TOCT | 0 | [NA] (nA)
| 1 | [PRESSURE] (PrESS)
| 2 | [FLOW] (FLOW)
| 3 | [OTHER] (OtHEr)
TUNU | 0 | [No] (nO)
| 1 | [Therm mot] (tM)
TWO | 0 | [OFF] (LOW)
| 1 | [ON] (HIGH)
URES | 20 | [200 Vac] (200)
| 22 | [220 Vac] (220)
| 23 | [230 Vac] (230)
| 24 | [240 Vac] (240)
| 38 | [380 Vac] (380)
| 40 | [400 Vac] (400)
| 44 | [440 Vac] (440)
| 46 | [460 Vac] (460)
| 48 | [480 Vac] (480)
| 52 | [525V ac] (525)
| 57 | [575 Vac] (575)
| 60 | [600 Vac] (600)
| 69 | [690 Vac] (690)
USB | 0 | [Error Triggered] (0)
| 1 | [Error Triggered w/o Relay] (1)
| 2 | [Warning Triggered] (2)
VCAL | 0 | [Unknown Voltage] (nO)
| 1 | [100-120(1)] (110M)
| 2 | [100-120(3)] (110t)
| 3 | [200-240 V single] (M2)
| 4 | [200-240 V Three] (M3)
| 5 | [380-500(1)] (480M)
| 6 | [380-500 V Three] (n4)
| 7 | [525-600(1)] (690M)
| 8 | [525-600 V Three] (S6)
WUPM | 0 | [FeedBack] (Fb )
| 1 | [Error] (Err)
| 2 | [Pressure] (LP)

## Registers
CMI |  | Bit 0 | Factory setting command (active at 1).
|  | Bit 1 | Save configuration to EEPROM non-volatile memory command (active at 1).
This Bit automatically changes to 0 after the request is taken into account. The command is only active if the drive is stopped, and not in "5-Operation enabled" state.
Note: If CMI is a periodic network variable, the PLC program must write it to 0 after the first request is taken into account. The life of the EEPROM memory is limited to 100,000 write operations.
Note: If the motor or configuration switching function is active, the configuration in the RAM is saved to the EEPROM in the configuration designated by [Config. Active] (CnFS).
|  | Bit 2 | Reserved (= 0).
|  | Bit 3 | Reserved (= 0).
|  | Bit 4 | Reserved (= 0).
|  | Bit 5 | Reserved (= 0).
|  | Bit 6 | Reserved (= 0).
|  | Bit 7 | Reserved (= 0).
|  | Bit 8 | Reserved (= 0).
|  | Bit 9 | Definition of the frequency reference (LFr) and output frequency (rFr) unit:
= 0: 0.1 Hz
= 1: Standardized value 16 signed bits based on the maximum frequency. The value 32767 corresponds to [Max frequency] (tFr). The default value of [Max frequency] (tFr) is 60 Hz, and the resolution is then approximately 0.0018 Hz.
This function has no effect on the speed reference (LFrd) or the output speed (rFrd).
|  | Bit 10 | Reserved (= 0).
|  | Bit 11 | Reserved (= 0).
|  | Bit 12 | Reserved (= 0).
|  | Bit 13 | Reserved (= 0).
|  | Bit 14 | Reserved (= 0).
|  | Bit 15 | Parameter consistency check
= 0: The check is activated. Each time a parameter is written, the drive checks the relationship between the written parameter and the configuration in the drive. For example, the [High speed] (HSP) parameter must be less than [Max frequency] (tFr).
= 1: The check is deactivated. The drive is locked in stop mode. In this drive state, the configuration can be written parameter by parameter and the drive does not modify the values that are written.
The switch from 1 to 0 triggers a calculation of the consistency of the configuration. Some parameters can be modified automatically by the drive.
CMD | Possible values in CiA402 profile, separate or not separate mode:
CMP0 |  | Bit 0 | Switch on/Contactor command.
CMP1 |  | Bit 1 | Disable voltage/Authorization to supply AC power.
CMP2 |  | Bit 2 | Quick stop/Emergency stop.
CMP3 |  | Bit 3 | Enable operation/Run command.
CMP4 |  | Bit 4 | Reserved (set to 0).
CMP5 |  | Bit 5 | Reserved (set to 0).
CMP6 |  | Bit 6 | Reserved (set to 0).
CMP7 |  | Bit 7 | Fault reset/Fault acknowledgment active on 0 to 1 rising edge.
CMP8 |  | Bit 8 | Halt Stop according to the [Type of stop] (Stt) parameter without leaving the Operation enabled state.
CMP9 |  | Bit 9 | Reserved (set to 0).
CMPA |  | Bit 10 | Reserved (set to 0).
CMPB |  | Bit 11 to 15 | Can be assigned to commands.
CMPC | Possible values in the IO profile on state command [2 wire] (2C).
CMPD |  | Bit 0 | Forward (on state) command
CMPE |  |  | = 0: No forward command
CMPF |  |  | = 1: Forward command
The assignment of Bit 0 cannot be modified. It corresponds to the assignment of the terminals. It can be switched. Bit 0 (Cd00) is only active if the channel of this control word is active.
|  | Bit 1 to 15 | Can be assigned to commands.
Possible values in the IO profile on edge command [3 wire] (3C).
|  | Bit 0 | Stop (run authorization).
= 0: Stop
= 1: Run is authorized on a forward or reverse command
|  | Bit 1 | Forward (on 0 to 1 rising edge) command.
The assignment of Bits 0 and 1 cannot be modified. It corresponds to the assignment of the terminals. It can be switched. Bits 0 (Cd00) and 1 (Cd01) are only active if the channel of this control word is active.
|  | Bit 2 to 15 | can be assigned to commands.
ETA | Possible values in CiA402 profile, separate or not separate mode:
EP0 |  | Bit 0 | = 1: "Ready to switch on", awaiting power section line supply
EP1 |  | Bit 1 | = 1: "Switched on", ready
EP2 |  | Bit 2 | = 1: "Operation enabled", running
EP3 |  | Bit 3 | = 1: Fault detection
EP4 |  | Bit 4 | "Voltage enabled", power section line supply present
EP5 |  |  | = 0: Power section line supply absent
EP6 |  |  | = 1: Power section line supply present
EP7 |  |  | When the drive is powered by the power section only, this bit is always at 1.
EP8 |  | Bit 5 | Bit 5: = 0: Quick stop/Emergency stop
EP9 |  | Bit 6 | Bit 6: = 1: "Switched on disabled", power section line supply locked
EPA |  | Bit 7 | Bit 7: Warning, alarm
EPB |  |  | = 0: No alarm
EPC |  |  | = 1: Alarm
EPD |  | Bit 8 | Bit 8: Reserved (= 0)
EPE |  | Bit 9 | Bit 9: Remote: command or reference via the network
EPF |  |  | = 0: Command or reference via the graphic display terminal or the remote display terminal
ETAD |  |  | = 1: Command or reference via the network
|  | Bit 10 | Bit 10: Target reference reached
= 0: The reference is not reached
= 1: The reference has been reached
When the drive is in speed mode, this is the speed reference.
|  | Bit 11 | Bit 11: "Internal limit active", reference outside limits
= 0: The reference is within the limits
= 1: The reference is not within the limits
When the drive is in speed mode, the limits are defined by the [Low speed] (LSP) and [High speed] (HSP) parameters.
|  | Bit 12 | Bit 12: Reserved (= 0)
|  | Bit 13 | Bit 13: Reserved (= 0)
|  | Bit 14 | Bit 14: "Stop key", STOP via stop key
= 0: STOP key not pressed
= 1: Stop triggered by the STOP key on the graphic display terminal or the remote display terminal
|  | Bit 15 | Bit 15: "Direction", direction of rotation
= 0: Forward rotation at output
= 1: Reverse rotation at output
The combination of Bits 0, 1, 2, 4, 5 and 6 defines the state in the DSP 402 state chart (see the Communication manuals).
ETI |  | Bit 0 | = 1: Access to the EEPROM non-volatile memory in progress
IP0
IP1
IP2 |  | Bit 1 | = 0: No parameter consistency check
IP3 |  |  | = 1: Parameter consistency check
IP4 |  | Bit 2 | = 0: The drive is not in fault state or a fault is detected
IP5 |  |  | = 1: The drive is in fault state but the fault is no longer present (not reset)
IP6 |  | Bit 3 | Bit 3: Reserved (= 0).
IP7 |  | Bit 4 | = 1: The drive is in speed mode
IP8 |  | Bit 5 | = 1: DC injection braking (identical to LSR4, bit 11)
IP9 |  | Bit 6 | = 0: Drive in steady state
IPA |  |  | = 1: Drive in transient state
IPB |  | Bit 7 | = 1: Motor thermal state threshold reached for the active motor
IPC |  | Bit 8 | = 1: Overbraking (identical to LSR5, bit 1)
IPD |  | Bit 9 | = 1: Acceleration in progress (identical to LSR4, bit 13)
IPE |  | Bit 10 | = 1: Deceleration in progress (identical to LSR4, bit 14)
IPF |  | Bit 11 | = 1: Current limit in progress
|  | Bit 12 | = 1: Fast stop in progress (identical to LSR4, bit 15)
|  | Bit 13 to 14 | bit 13 = 0 and bit 14 = 0: Drive controled by terminal
bit 13 = 1 and bit 14 = 0: Drive controled by remote keypad
bit 13 = 0 and bit 14 = 1: Drive controled by Modbus
bit 13 = 1 and bit 14 = 1: Drive controled by CANopen or the network card
|  | Bit 15 | = 0: Forward operation applied before the ramp
= 1: Reverse operation applied before the ramp
CRC |  | Bit 0 | = 1 : Terminal board
CCC |  | Bit 1 | = 1 : Local keypad
|  | Bit 2 | = 1 : Deported keypad
|  | Bit 3 | = 1 : Modbus
|  | Bit 4 | Reserved
|  | Bit 5 | Reserved
|  | Bit 6 | = 1 : CANopen
|  | Bit 7 | = 1 : Terminal up-Down speed
|  | Bit 8 | = 1 : Deported keypad up-down speed
|  | Bit 9 | = 1 : COM option board
|  | Bit 10 | Reserved
|  | Bit 11 | = 1 : Embedded Ethernet
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | = 1 : Indus
|  | Bit 15 | = 1 : PowerSuite
IL1R |  | Bit 0 | "LI1" logic inputs real image
|  | Bit 1 | "LI2" logic inputs real image
|  | Bit 2 | "LI3" logic inputs real image
|  | Bit 3 | "LI4" logic inputs real image
|  | Bit 4 | "LI5" logic inputs real image
|  | Bit 5 | "LI6" logic inputs real image
|  | Bit 6 | "LI7" logic inputs real image
|  | Bit 7 | "LI8" logic inputs real image
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | "LI11" logic inputs real image
|  | Bit 11 | "LI12" logic inputs real image
|  | Bit 12 | "LI13" logic inputs real image
|  | Bit 13 | "LI14" logic inputs real image
|  | Bit 14 | "LI15" logic inputs real image
|  | Bit 15 | "LI16" logic inputs real image
OL1R |  | Bit 0 | "R1" relay real image
|  | Bit 1 | "R2" relay real image
|  | Bit 2 | "R3" relay real image
|  | Bit 3 | "R4" relay real image
|  | Bit 4 | "R5" relay real image
|  | Bit 5 | "R6" relay real image
|  | Bit 6 | Reserved
|  | Bit 7 | Reserved
|  | Bit 8 | "DO1" logic outputs real image
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | "DO11" logic outputs real image
|  | Bit 13 | "DO12" logic outputs real image
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
CIC |  |  | On power-up, read CIC :
If CIC and CIC2 = 0 -> Ok
If CIC or CIC2 not 0 -> malfunction
Write FCS = "INI" to return to factory setting
|  | Bit 0 | = 1 : Power board changed
|  | Bit 1 | = 1 : COM option card added
|  | Bit 2 | = 1 : COM option card removed
|  | Bit 3 | = 1 : Loaded config invalid
|  | Bit 4 | = 1 : COM option card changed
|  | Bit 5 | = 1 : APP option card added
|  | Bit 6 | = 1 : APP option card removed
|  | Bit 7 | = 1 : APP option card changed
|  | Bit 8 | = 1 : IO option card added
|  | Bit 9 | = 1 : IO option card removed
|  | Bit 10 | = 1 : IO option card changed
|  | Bit 11 | = 1 : ENC option card added
|  | Bit 12 | = 1 : ENC option card removed
|  | Bit 13 | = 1 : ENC option card changed
|  | Bit 14 | Reserved
|  | Bit 15 | = 1 : Control board changed
CRP0 | Bit 0 to Bit 7: Active command channels
CRP1 |  | =0 : The terminal board is the active channel.
CRP2 |  | =1 : The local keypad is the active channel.
CRP3 |  | =2 : The remote keypad is the active channel.
CRP4 |  | =3 : Modbus is the active channel.
CRP5 |  | =4 : Reserved
CRP6 |  | =5 : Reserved
CRP7 |  | =6 : CANopen is the active channel.
CRP8 |  | =7 : The terminals are the active channel in the +/- speed reference.
CRP9 |  | =8 : The remote keypad is the active channel (up-down speed)
CRPA |  | =9 : The network card is the active channel.
CRPB |  | =10 : Reserved
CRPC |  | =11 : Reserved
CRPD |  | =12 : Reserved
CRPE |  | =13 : Reserved
CRPF |  | =14 : Reserved
=15 : SoMove software is the active channel.
Bit 8 to Bit 15: Active reference channels
=0 : The terminals are the active channel via an analog input.
=1 : The local keypad is the active channel.
=2 : The remote keypad is the active channel.
=3 : Modbus is the active channel.
=4 : Reserved
=5 : Reserved
=6 : CANopen is the active channel.
=7 : The terminals are the active channel in the +/- speed reference.
=8 : The remote keypad is the active channel (up-down speed)
=9 : The network card is the active channel.
=10 : Reserved
=11 : Reserved
=12 : Reserved
=13 : Reserved
=14 : Reserved
=15 : SoMove software is the active channel.
FRY |  | Bit 0 | = 1 : All parameters
|  | Bit 1 | = 1 : Drive configuration
|  | Bit 2 | Reserved
|  | Bit 3 | = 1 : Motor parameters
|  | Bit 4 | = 1 : Communication menu
|  | Bit 5 | Reserved
|  | Bit 6 | Reserved
|  | Bit 7 | = 1 : Display menu
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved (Bit15 = 1 : Communication option parameters)
EWE |  | Bit 0 | = 1 : Enable Web
|  | Bit 1 | = 1 : Enable Email
IL1I |  | Bit 0 | "LI1" logic inputs physical image
|  | Bit 1 | "LI2" logic inputs physical image
|  | Bit 2 | "LI3" logic inputs physical image
|  | Bit 3 | "LI4" logic inputs physical image
|  | Bit 4 | "LI5" logic inputs physical image
|  | Bit 5 | "LI6" logic inputs physical image
|  | Bit 6 | "LI7" logic inputs physical image
|  | Bit 7 | "LI8" logic inputs physical image
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | "LI11" logic inputs physical image
|  | Bit 11 | "LI12" logic inputs physical image
|  | Bit 12 | "LI13" logic inputs physical image
|  | Bit 13 | "LI14" logic inputs physical image
|  | Bit 14 | "LI15" logic inputs physical image
|  | Bit 15 | "LI16" logic inputs physical image
PEV1 |  | Bit 0 | = 1 : first mapped Object
|  | Bit 1 | = 1 : second mapped Object
|  | Bit 2 | = 1 : third mapped Object
|  | Bit 3 | = 1 : fourth mapped Object
|  | Bit 4 | Reserved
|  | Bit 5 | Reserved
|  | Bit 6 | Reserved
|  | Bit 7 | Reserved
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
PEV2 |  | Bit 0 | = 1 : first mapped Object
|  | Bit 1 | = 1 : second mapped Object
|  | Bit 2 | = 1 : third mapped Object
|  | Bit 3 | = 1 : fourth mapped Object
|  | Bit 4 | Reserved
|  | Bit 5 | Reserved
|  | Bit 6 | Reserved
|  | Bit 7 | Reserved
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
PEV3 |  | Bit 0 | = 1 : first mapped Object
|  | Bit 1 | = 1 : second mapped Object
|  | Bit 2 | = 1 : third mapped Object
|  | Bit 3 | = 1 : fourth mapped Object
|  | Bit 4 | Reserved
|  | Bit 5 | Reserved
|  | Bit 6 | Reserved
|  | Bit 7 | Reserved
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
PEV4 |  | Bit 0 | = 1 : first mapped Object
|  | Bit 1 | = 1 : second mapped Object
|  | Bit 2 | = 1 : third mapped Object
|  | Bit 3 | = 1 : fourth mapped Object
|  | Bit 4 | Reserved
|  | Bit 5 | Reserved
|  | Bit 6 | Reserved
|  | Bit 7 | Reserved
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
ST00 |  | Bit 0 | (JAMP) : An anti-jam request is pending
|  | Bit 1 | (JAMR) : An anti-jam sequence is running
|  | Bit 2 | (FILL) : Pipe fill sequence is running
|  | Bit 3 | (IPPC) : Inlet pressure compensation is running
|  | Bit 4 | (SLM) : Stop asked by a "sleeping" function
|  | Bit 5 | (LDA) : Low demand active (Wave 2)
|  | Bit 6 | (PPON) : Priming pump is running
|  | Bit 7 | (JPON) : Jockey pump is running
|  | Bit 8 | (SLPP) : Sleep is pending
|  | Bit 9 | (SLPB) : Sleep Boost phase is running
|  | Bit 10 | (SLP) : Application Sleeping
|  | Bit 11 | (ASLC) : Advanced Sleep Checking is active
ST02 |  | Bit 0 | (CNF0) : Configuration 1 is used
|  | Bit 8 | (CFP1) : Parameter set 1 is used
|  | Bit 9 | (CFP2) : Parameter set 2 is used
|  | Bit 10 | (CFP3) : Parameter set 3 is used
|  | Bit 11 | (CFP4) : Parameter set 4 is used
ST03 |  | Bit 0 | (FLO) : Drive in forced local mode
|  | Bit 1 | (FR2) : Reference channel is channel 2
|  | Bit 2 | (FR1B) : Reference channel is channel 1, and FR1B is used
|  | Bit 3 | (FR1) : Reference channel is channel 1 (FR1 or FR1B is used)
|  | Bit 4 | (CD1) : Command channel is channel 1
|  | Bit 5 | (CD2) : Command channel is channel 2
|  | Bit 6 | (RFC) : Reference channel : 0-> channel1, 1-> channel 2
|  | Bit 7 | (RCB) : 0: FR1, FR1B ?
|  | Bit 8 | (CCS) : Command channel : 0-> channel 1, 1-> channel 2
|  | Bit 9 | (BMP) : Bump Less Channel
ST04 |  | Bit 0 | (FLT) : Drive is in fault state
|  | Bit 1 | (AUTO) : Automatic restart attempts in progress
|  | Bit 2 | (RDY) : Drive is in ready state
|  | Bit 3 | (RUN) : A gating order is set (there is potentially current in the motor)
|  | Bit 4 | (DBL) : Powerstage is supply (DC bus charged)
|  | Bit 5 | (CTL) : Controlled stop on power loss in progress
|  | Bit 6 | (STO) : STO function activated
|  | Bit 7 | (FST) : A fast stop request is on going
|  | Bit 8 | (FRF) : Reaction on event / fallback speed
|  | Bit 9 | (RLS) : Reaction on event / maintain speed
|  | Bit 10 | (STT) : Reaction on event / Stop on STT without tripping in fault
|  | Bit 11 | (IDLE) : Stop and Go idle state (FF343)
ST05 |  | Bit 0 | (LLC) : The drive asks to close the line contactor
|  | Bit 2 | (SOC) : The drive has detected that the output contactor is open (Uncontrolled downstream contactor)
|  | Bit 6 | (CBEP) : The drive asks to close the circuit breaker
|  | Bit 7 | (CBDP) : The drive asks to open the circuit breaker
ST06 |  | Bit 0 | (ACC) : Drive in acceleration
|  | Bit 1 | (DEC) : Drive in deceleration
|  | Bit 2 | (SRA) : Frequency reference reached
|  | Bit 3 | (MFRD) : Motor running in Forward
|  | Bit 4 | (MRRS) : Motor running in Reverse
|  | Bit 5 | (ATS) : Torque on the motor is negative
|  | Bit 6 | (IDC) : DC injection is running (automatic or by order)
|  | Bit 9 | (TUN) : Autotune in progress
|  | Bit 10 | (MCP) : Motor current present
|  | Bit 11 | (RP2) : Ramp switching state : 0-> ramp 1, 1-> ramp 2
ST07 |  | Bit 0 | (AG1) : One of the alarm of alarm group 1 is active
|  | Bit 1 | (AG2) : One of the alarm of alarm group 2 is active
|  | Bit 2 | (AG3) : One of the alarm of alarm group 3 is active
|  | Bit 3 | (AG4) : One of the alarm of alarm group 4 is active
|  | Bit 4 | (AG5) : One of the alarm of alarm group 5 is active
|  | Bit 8 | (LCA1) : Life Cycle Alarm 1 alarm
|  | Bit 9 | (LCA2) : Life Cycle Alarm 2 alarm
ST08 |  | Bit 0 | (DRYA) : Dry Running Alarm
|  | Bit 1 | (PLFA) : Pump Low Flow Alarm
|  | Bit 2 | (HFPA) : High Flow Alarm
|  | Bit 3 | (IPPA) : Inlet Pressure Protection Alarm
|  | Bit 4 | (OPLA) : Outlet Pressure Low Alarm
|  | Bit 5 | (OPHA) : Outlet Pressure High Alarm
|  | Bit 6 | (PCPA) : Cyclic Start Protection Alarm
|  | Bit 7 | (JAMA) : Antijam alarm is raised
|  | Bit 8 | (LFA) : Low Flow Alarm
|  | Bit 9 | (LPA) : Low pressure alarm is raised
|  | Bit 10 | (FSA) : Flow limit function activated (FL_Mode_On)
|  | Bit 11 | (OPSA) : Outlet Pressure High Switch Alarm
|  | Bit 12 | (MPCA) : Multi-pumps Capacity Alarm
|  | Bit 13 | (MPLA) : Multi-pumps Lead Alarm
|  | Bit 14 | (LCHA) : Level Control High Level Alarm
|  | Bit 15 | (LCLA) : Level Control Low Level Alarm
ST09 |  | Bit 0 | (PFA) : alarm on PID Feedback
|  | Bit 1 | (PFAH) : PID feedback high threshold reached
|  | Bit 2 | (PFAL) : PID feedback low threshold reached
|  | Bit 3 | (PISH) : PI feedback monitoring alarm is raised
|  | Bit 4 | (LCWA) : Level Control Switch Failure Alarm
|  | Bit 11 | (PEE) : alarm on PID error
ST11 |  | Bit 0 | (TP2A) : Temperature Protection AI2 Alarm
|  | Bit 1 | (TP3A) : Temperature Protection AI3 Alarm
|  | Bit 2 | (TP4A) : Temperature Protection AI4 Alarm
|  | Bit 3 | (TP5A) : Temperature Protection AI5 Alarm
ST12 |  | Bit 0 | (AP1) : 4-20 loss alarm on AI1
|  | Bit 1 | (AP2) : 4-20 loss alarm on AI2
|  | Bit 2 | (AP3) : 4-20 loss alarm on AI3
|  | Bit 3 | (AP4) : 4-20 loss alarm on AI4
|  | Bit 4 | (AP5) : 4-20 loss alarm on AI5
ST13 |  | Bit 0 | (THA) : drive overheating alarm is raised
|  | Bit 1 | (TJA) : alarm on IGBT thermal state
|  | Bit 2 | (FCTA) : Fan Counter Speed alarm
|  | Bit 3 | (FFDA) : Fan feedback alarm is raised
|  | Bit 5 | (EFA) : external alarm is raised
|  | Bit 6 | (USA) : undervoltage alarm is raised
|  | Bit 7 | (UPA) : controlled stop on power loss threshold id reached
|  | Bit 8 | (OBR) : Impossible to follow the customer ramp during deceleration
|  | Bit 9 | (URA) : Intelligent Rectifier alarm is raised
ST14 |  | Bit 0 | (FTA) : Motor frequency high threshold 1 reached
|  | Bit 1 | (FTAL) : Motor frequency low threshold 1 reached
|  | Bit 3 | (F2AL) : Motor frequency low threshold 2 reached
|  | Bit 4 | (FLA) : HighSpeedReached function result
|  | Bit 5 | (RTAH) : Reference frequency high threshold reached
|  | Bit 6 | (RTAL) : Reference frequency low threshold reached
|  | Bit 7 | (F2A) : Motor frequency high threshold 2 reached
|  | Bit 15 | (INWM) : Ethernet Internal Warning
ST15 |  | Bit 0 | (CTA) : Motor current high threshold reached
|  | Bit 1 | (CTAL) : Motor current low threshold reached
|  | Bit 2 | (TTHA) : Motor torque high threshold reached
|  | Bit 3 | (TTLA) : Motor torque low threshold reached
|  | Bit 4 | (ULA) : Underload is detected
|  | Bit 5 | (OLA) : Overload is detected
|  | Bit 6 | (CLI) : current or torque limitation is running
|  | Bit 9 | (POWD) : Electrical Power Drift alarm
|  | Bit 10 | (PTHA) : Power high threshold reached
|  | Bit 11 | (PTHL) : Power Low threshold reached
ST16 |  | Bit 1 | (TAD) : DriveThermalThresholdReached function result
|  | Bit 2 | (TSA) : MotorThermalThresholdReached function result (motor 1)
ST17 |  | Bit 0 | (CAS1) : Customer Alarm 1 active
|  | Bit 1 | (CAS2) : Customer Alarm 2 active
|  | Bit 2 | (CAS3) : Customer Alarm 3 active
|  | Bit 3 | (CAS4) : Customer Alarm 4 active
|  | Bit 4 | (CAS5) : Customer Alarm 5 active
|  | Bit 14 | (DRAP) : Device Replacement Activated but not plugged
|  | Bit 15 | (DRTF) : Device Replacement Transfert Failure
ST18 |  | Bit 0 | (FCBA) : AFE : Fan running time
|  | Bit 1 | (FFBA) : AFE : Fan frequency
|  | Bit 2 | (CLIM) : AFE : Current or power limitation is running in motor mode
|  | Bit 3 | (CLIG) : AFE : Current or power limitation is running in generator mode
|  | Bit 4 | (THSA) : AFE : Sensor thermal state
|  | Bit 5 | (THJA) : AFE : IGBT thermal state
|  | Bit 6 | (FFCA) : MCE : Cabinet fan alarm state
|  | Bit 7 | (FCCA) : MCE : Cabinet fan alarm running time
|  | Bit 8 | (CHA) : MCE : Cabinet over-heating alarm
|  | Bit 9 | (CMIJ) : MCE : CMI jumper is closed
ST19 |  | Bit 0 | (IWA) : IO function : Digital warning A
|  | Bit 1 | (IWB) : IO function : Digital warning B
|  | Bit 2 | (IWC) : IO function : Digital warning C
|  | Bit 3 | (IWD) : IO function : Digital warning D
|  | Bit 4 | (CWA) : IO function : Cabinet warning A
|  | Bit 5 | (CWB) : IO function : Cabinet warning B
|  | Bit 6 | (CWC) : IO function : Cabinet warning C
|  | Bit 7 | (TWA) : IO function : Thermal input warning A
|  | Bit 8 | (TWB) : IO function : Thermal input warning B
|  | Bit 9 | (TWC) : IO function : Thermal input warning C
|  | Bit 10 | (TWD) : IO function : Thermal input warning D
|  | Bit 11 | (CBW) : Circuit breaker : Error state (not in accordance to the start and stop pulse)
ILCI |  | Bit 0 | "DI50" logic inputs physical image
|  | Bit 1 | "DI51" logic inputs physical image
|  | Bit 2 | "DI52" logic inputs physical image
|  | Bit 3 | "DI53" logic inputs physical image
|  | Bit 4 | "DI54" logic inputs physical image
|  | Bit 5 | "DI55" logic inputs physical image
|  | Bit 6 | "DI56" logic inputs physical image
|  | Bit 7 | "DI57" logic inputs physical image
|  | Bit 8 | "DI58" logic inputs physical image
|  | Bit 9 | "DI59" logic inputs physical image
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
ILCR |  | Bit 0 | "DI50" logic inputs real image
|  | Bit 1 | "DI51" logic inputs real image
|  | Bit 2 | "DI52" logic inputs real image
|  | Bit 3 | "DI53" logic inputs real image
|  | Bit 4 | "DI54" logic inputs real image
|  | Bit 5 | "DI55" logic inputs real image
|  | Bit 6 | "DI56" logic inputs real image
|  | Bit 7 | "DI57" logic inputs real image
|  | Bit 8 | "DI58" logic inputs real image
|  | Bit 9 | "DI59" logic inputs real image
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
OLCI |  | Bit 0 | "R60" relay physical image
|  | Bit 1 | "R61" relay physical image
|  | Bit 2 | "R62" relay physical image
|  | Bit 3 | "R63" relay physical image
|  | Bit 4 | "R64" relay physical image
|  | Bit 5 | "R65" relay physical image
|  | Bit 6 | "R66" relay physical image
|  | Bit 7 | Reserved
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
OLCR |  | Bit 0 | "R60" relay real image
|  | Bit 1 | "R61" relay real image
|  | Bit 2 | "R62" relay real image
|  | Bit 3 | "R63" relay real image
|  | Bit 4 | "R64" relay real image
|  | Bit 5 | "R65" relay real image
|  | Bit 6 | "R65" relay real image
|  | Bit 7 | Reserved
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
BPI0 |  | Bit 0 | Fault in power brick 1
BPI1
BPI2
BPI3
BPI4
BPI5 |  | Bit 1 | Fault in power brick 2
BPI6 |  | Bit 2 | Fault in power brick 3
BPI7 |  | Bit 3 | Fault in power brick 4
BPI8 |  | Bit 4 | Fault in power brick 5
BPI9 |  | Bit 5 | Fault in power brick 6
BPIA |  | Bit 6 | Fault in power brick 7
BPIB |  | Bit 7 | Fault in power brick 8
BPIC |  | Bit 8 | Fault in power brick 9
BPID |  | Bit 9 | Fault in power brick 10
BPIE |  | Bit 10 | Fault in power brick 11
BPIF |  | Bit 11 | Fault in power brick 12
BFI0 |  | Bit 0 | Fault in AFE brick 1
BFI1
BFI2
BFI3
BFI4
BFI5 |  | Bit 1 | Fault in AFE brick 2
BFI6 |  | Bit 2 | Fault in AFE brick 3
BFI7 |  | Bit 3 | Fault in AFE brick 4
BFI8 |  | Bit 4 | Fault in AFE brick 5
BFI9 |  | Bit 5 | Fault in AFE brick 6
BFIA |  | Bit 6 | Fault in AFE brick 7
BFIB |  | Bit 7 | Fault in AFE brick 8
BFIC |  | Bit 8 | Fault in AFE brick 9
BFID |  | Bit 9 | Fault in AFE brick 10
BFIE |  | Bit 10 | Fault in AFE brick 11
BFIF |  | Bit 11 | Fault in AFE brick 12
CIC2 |  |  | On power-up, read CIC :
If CIC and CIC2 = 0 -> Ok
If CIC or CIC2 not 0 -> malfunction
Write FCS = "INI" to return to factory setting
|  | Bit 0 | = 1 : SFTY option card added
|  | Bit 1 | = 1 : SFTY option card removed
|  | Bit 2 | = 1 : SFTY option card changed
|  | Bit 3 | Reserved
|  | Bit 4 | Reserved
|  | Bit 5 | Reserved
|  | Bit 6 | Reserved
|  | Bit 7 | Reserved
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
ST20 |  | Bit 1 | (MPDA) : Master Slave : Device loss